## Duct System Sizer (hidden)
System: | CPEF
Level | Room Type 1 |  |  |  | Room Type 2 |  |  |  | Room Type 3 |  |  |  | Room Type4 |  |  |  | Room Type 5 |  |  |  | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s | Supply air | Exhaust 1 | Exhaust 2
B1 | Room Type 1 NO.: 6; Room Type 1 Rate: 400
| Room Type 1 Flow: 2400; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 2400 | 0.2 | 0.2 | 60 | 1920 | 1050 | 1950
G | Room Type 1 NO.: 2; Room Type 1 Rate: 450; Room Type 2 NO.: 4; Room Type 2 Rate: 450
| Room Type 1 Flow: 900; Room Type 2 Flow: 1800; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 2700 | 0 | 0 | #DIV/0! | 2160 | 945 | 1755
L1 | Room Type 1 NO.: 4; Room Type 1 Rate: 500; Room Type 2 NO.: 4; Room Type 2 Rate: 750
| Room Type 1 Flow: 2000; Room Type 2 Flow: 3000; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 5000 | 1.5 | 0.4 | 8.3333 | 4000 | 2000 | 3000
[21 empty] | 10100 | 1 | 1.8 | 5.6111 | 8080
[21 empty] | 10100 | 0.5 | 0.2 | 101
System: | Room Type 1 NO.: CPSF-2, S
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.5 | 0.3 | 0 | 672
G | Room Type 1 NO.: 5; Room Type 1 Rate: 152
| Room Type 1 Flow: 760; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 760 | 0 | 0 | #DIV/0! | 756
L1 | Room Type 1 NO.: 5; Room Type 1 Rate: 200
| Room Type 1 Flow: 1000; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1000 | 0 | 0 | #DIV/0! | 1400
[21 empty] | 1760 | 1 | 0.8 | 2.2 | 2828
[21 empty] | 1760 | 1.2 | 0.75 | 1.9556
System: | Room Type 1 NO.: CPSF-1, N
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1 | Room Type 1 NO.: 11; Room Type 1 Rate: 175
| Room Type 1 Flow: 1925; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1925 | 0.8 | 0.3 | 8.0208 | 1248
G | Room Type 1 NO.: 9; Room Type 1 Room: Ensuite; Room Type 1 Rate: 155
| Room Type 1 Flow: 1395; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1395 | 0.7 | 0.3 | 6.6429 | 1404
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.25 | 0.2 | 0 | 2600
[21 empty] | 3320 | 0.8 | 1 | 4.15 | 5252
[21 empty] | 3320 | 1 | 2 | 1.66
System: | Room Type 1 NO.: FPSF-1
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
G | Room Type 1 NO.: 2; Room Type 1 Rate: 750
| Room Type 1 Flow: 1500; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1500 | 0.7 | 0.3 | 7.1429
[21 empty] | 1500 | 0.7 | 0.3 | 7.1429
[21 empty] | 1500 | 1.2 | 0.4 | 3.125
System: | Room Type 1 NO.: SAF-G-3
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
G | Room Type 1 NO.: 2; Room Type 1 Rate: 75
| Room Type 1 Flow: 150; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 150 | 0.7 | 0.3 | 0.71429
[21 empty] | 150 | 0.7 | 0.3 | 0.71429
[21 empty] | 150 | 1.2 | 0.4 | 0.3125
System: | Room Type 1 NO.: SAF-G-1
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G | Room Type 1 NO.: 2; Room Type 1 Room: Store; Room Type 1 Rate: 75
| Room Type 1 Flow: 150; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 150 | 0.2 | 0.2 | 3.75
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
[21 empty] | 150 | 0.4 | 0.2 | 1.875
System: | Room Type 1 NO.: SAF-G-2
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G | Room Type 1 NO.: 1; Room Type 1 Room: Store; Room Type 1 Rate: 15
| Room Type 1 Flow: 15; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 15 | 0.2 | 0.2 | 0.375
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
[21 empty] | 15 | 0.4 | 0.2 | 0.1875
System: | Room Type 1 NO.: GEF-R-1
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G | Room Type 1 NO.: 2; Room Type 1 Room: Garbage; Room Type 1 Rate: 120
| Room Type 1 Flow: 240; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 240 | 0.3 | 0.3 | 2.6667
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
[21 empty] | 240 | 0.25 | 0.25 | 3.84
System: | Room Type 1 NO.: TEF-R-6
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
L1 | Room Type 1 NO.: 5; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 200; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 200 | 0.2 | 0.2 | 5
L2 | Room Type 1 NO.: 5; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 200; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 200 | 0.2 | 0.2 | 5
[21 empty] | 400 | 0.3 | 0.2 | 6.6667
System: | Room Type 1 NO.: TEF-R-7
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1 | Room Type 1 NO.: 6; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 240; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 240 | 0.3 | 0.2 | 4
L2 | Room Type 1 NO.: 6; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 240; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 240 | 0.3 | 0.2 | 4
[21 empty] | 480 | 0.3 | 0.3 | 5.3333
System: | Room Type 1 NO.: TEF-R-8
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1 | Room Type 1 NO.: 2; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 80; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 80 | 0.2 | 0.15 | 2.6667
L2 | Room Type 1 NO.: 2; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 80; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 80 | 0.2 | 0.15 | 2.6667
[21 empty] | 160 | 0.2 | 0.2 | 4
System: | Room Type 1 NO.: TEF-R-9
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1 | Room Type 1 NO.: 4; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 160; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 160 | 0.2 | 0.2 | 4
L2 | Room Type 1 NO.: 4; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 160; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 160 | 0.2 | 0.2 | 4
[21 empty] | 320 | 0.3 | 0.2 | 5.3333
System: | Room Type 1 NO.: GEF-B-2
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1 | Room Type 1 NO.: 1; Room Type 1 Room: MSR; Room Type 1 Rate: 90
| Room Type 1 Flow: 90; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 90 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.2 | 0.2 | 0
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.2 | 0.2 | 0
[21 empty] | 90 | 0.2 | 0.15 | 3
[21 empty] | 90 | 0.3 | 0.15 | 2

## Mechanical Design Certificate
Mechanical Design Certificate
Pursuant to the provisions of Clause A5G3 of the National Construction Code 2022, Volume 1. | [7 empty] | Pursuant to the provisions of Clause A5.2 of the National Construction Code 2019 Admt 1, Volume 1.
I | Qing Felix Ye |  | of | Premium Consulting Engineers
| (Appropriately qualified person) |  |  | (Firm)
Suite 802, 299 Sussex Street, Sydney NSW 2000
(Address)
Qualifications and experience:
Master of HVAC Engineering, Chartered Professional Engineer (MIEAust No.: 3631369);
NSW Fair Trading C9 Certifier (Reg No.: BDC04672); and
NSW Fair Trading Mechanical Design Practitioner (Reg No.: DEP0000275)
Hereby certify:
That the Mechanical Services Drawings and Specifications have been checked and comply with:
• | The relevant clauses of the National Construction Code 2022. | [6 empty] | • | The relevant clauses of the National Construction Code 2019 Amendment 1.
| BCA Clause |  | Description (Mechanical) | [5 empty] | BCA Clause | Description (Mechanical)
| Specification 7(S7C5) |  | Fire Resistance Fire Hazard Property Air-handling ductwork | [5 empty] | Specification C1.10(5) | Fire Resistance Fire Hazard Property Air-handling ductwork
| C2D11 |  | Fire Resistance Fire Hazard Property Air-handling ductwork | [5 empty] | C1.10(5) | Fire Resistance Fire Hazard Property Air-handling ductwork
| C4D10 |  | Fire Resistance Protection of openings Service penetrations in fire-isolated exits | [5 empty] | C3.9 | Fire Resistance Protection of openings Service penetrations in fire-isolated exits
| C4D13 |  | Fire resistance Protection of Openings Openings in floors and ceilings for services | [5 empty] | C3.12 | Fire resistance Protection of Openings Openings in floors and ceilings for services
| C4D15 |  | Fire resistance Protection of Openings Openings for service installations | [5 empty] | C3.15 | Fire resistance Protection of Openings Openings for service installations
| E2D3 |  | Smoke Hazard Management General requirements Air Handling Systems | [5 empty] | E2.2 (a), (b)& (c) | Smoke Hazard Management General requirements Air Handling Systems
| F6D6 |  | Health and Amenity Light and Ventilation Ventilation of rooms | [5 empty] | F4.5 | Health and Amenity Light and Ventilation Ventilation of rooms
| F6D7 |  | Health and amenity Light and ventilation Natural Ventilation | [5 empty] | F4.6 | Health and amenity Light and ventilation Natural Ventilation
| F6D11 |  | Health and Amenity Light and Ventilation Carparks | [5 empty] | F4.11 | Health and Amenity Light and Ventilation Carparks
| F6D12 |  | Health and Amenity Light and Ventilation Kitchen local exhaust ventilation | [5 empty] | F4.12 | Health and Amenity Light and Ventilation Kitchen local exhaust ventilation
| F8D4 |  | Health and amenity Condensation management Flow rate and discharge of exhaust systems | [5 empty] | F6.3 | Health and amenity Condensation management Flow rate and discharge of exhaust systems
| J5D6 |  | Energy Efficiency Building Sealing Exhaust Fans | [5 empty] | J3.5 | Health and amenity Condensation Management Ventilation of roof spaces
| J6 |  | Energy Efficiency Air-conditioning and Ventilation Systems | [5 empty] | J5 | Energy Efficiency Air-conditioning and Ventilation Systems
| NSW E2D16 |  | Automatic Shutdown
• | The referenced Australian Standards listed in the Building Code of Australia (Schedule 4 Referenced Documents) as follows:
| Standard |  | Description (Mechanical) | [5 empty] | Standard | Description (Mechanical)
| AS1668.1:2015 |  | The use of ventilation and airconditioning in Buildings Part 1: Fire and Smoke Control in buildings | [5 empty] | AS1668.1:2015 | The use of ventilation and airconditioning in Buildings Part 1: Fire and Smoke Control in buildings
| AS1668.2:2012 |  | The use of ventilation and air conditioning in buildings Part 2: Mechanical ventilation for acceptable indoor-air quality | [5 empty] | AS1668.2:2012 | The use of ventilation and air conditioning in buildings Part 2: Mechanical ventilation for acceptable indoor-air quality
| AS1668.4:2012 |  | The use of ventilation and air conditioning in buildings Part 4: Natural ventilation of the buildings | [5 empty] | AS1668.4:2012 | The use of ventilation and air conditioning in buildings Part 4: Natural ventilation of the buildings
| 4254.1:2012 |  | Ductwork for Air-Handling Systems in Buildings - Flexible Duct | [5 empty] | AS5149.1:2016 | Refrigerating systems and heat pumps - Safety and environmental requirements Part 1: Definitions, classification and selection criteria
| 4254.2:2012 |  | Ductwork for Air-Handling Systems in Buildings - Rigid Duct | [5 empty] | AS5149.2:2016 | Refrigerating systems and heat pumps - Safety and environmental requirements Part 2: Design, construction, testing, marking and documentation
[9 empty] | AS3666.1:2011 | Air-handling and water systems of buildings — Microbial control
[9 empty] | 4254.1:2012 | Ductwork for Air-Handling Systems in Buildings - Flexible Duct
[9 empty] | 4254.2:2012 | Ductwork for Air-Handling Systems in Buildings - Rigid Duct
The following is a schedule of the relevant service design drawings and specifications.
| Drawing Number |  | Drawing Name |  |  |  | Revision
| M-000 |  | Cover Sheet |  |  |  | A
| M-001 |  | Tenancy Level Layout |  |  |  | A
| M-002 |  | Roof Layout |  |  |  | A
Yours faithfully,
Name: |  | Qing Ye (Felix) |  |  | Date: | 2024-03-01
Note: drawing list auto-copied from '01-Project Info' section.
Please select the clauses from the following list to suit the porject.

## Mechanical Desig Compliance
Mechanical Design Compliance Certificate
Pursuant to the provisions of Clause A5.2 of the Building Code of Australia Amendament 1, Volume 1.
I | Qing Felix Ye |  | of | Premium Consulting Engineers
| (Appropriately qualified person) |  |  | (Firm)
Suite 802, 299 Sussex Street, Sydney NSW 2000
(Address)
Qualifications and experience:
Master of HVAC Engineering, Chartered Professional Engineer (MIEAust No.: 3631369);
NSW Fair Trading C9 Certifier (Reg No.: BDC04672); and
NSW Fair Trading Mechanical Design Practitioner (Reg No.: DEP0000275)
Hereby certify:
The Mechanical system installation on site to date has to the best of our knowledge and belief, confirmed that the works designed and installed have been in accordance with the requirements of the design intent expressed in the design prepared by Premium Consulting Engineers Pty Ltd.
Subject to effective and thorough implementation of advice issued by Premium Consulting Engineers and to the extent that can reasonably be expected based on our inspections of visible work, we confirm our opinion that the works appear to have been undertaken in accordance with the intent of our documentation.
The following is a schedule of the relevant service design drawings and specifications.
| Drawing Number |  | Drawing Name |  |  |  | Revision
| M-000 |  | Cover Sheet |  |  |  | A
| M-001 |  | Tenancy Level Layout |  |  |  | A
| M-002 |  | Roof Layout |  |  |  | A
Yours faithfully,
Name: |  | Qing Ye (Felix) |  |  | Date: | 2024-03-01

## 01-AC Load
Load Calculation | [5 empty] | AC selection |  |  | Grille sizing
Room Name | Unit | Load rate | Cooling Load | Room Total Cooling | Room Total OA | FCU Modle | Cooling | Air Flow | Room Air flow | Grille Qty | Grille flowrate | Grille Size Rounded
|  | W/m2 | kW | kW | l/s |  | kW | l/s | l/s | # | l/s | l/s
TENANCY, AREA 1
KITCHEN | 175 | 90 | 15.75
Equipment |  |  | 0
Water |  |  | 0
Light | 175 | 15 | 2.625
People | 21.875 | 120 | 2.625
O/A=E/A | 164.0625 | 0.0305 | 5.0039
KITCHEN Summary | 175 | 148.5938 |  | 26.0039 | 164.0625 | FDYAN100AV1 | 10 | 800 | 800 | 2 | 400
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
TOTAL | 175 | 148.5938 |  | 26.0039 | 164.0625 | Total FCU Capacity: | 10 | 800 |  | 7 | 400 | 0
[5 empty] | 21.875 | VRV CU Selection
[6 empty] | PLEASE SELECT | 0 | -
TENANCY, AREA 2
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 2 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
TOTAL | 0 | - |  | 0 | 0 | Total FCU Capacity: | 0 | 0 |  | 7 | 0 | 0
[5 empty] | 0 | VRV CU Selection
[6 empty] | PLEASE SELECT | 0 | -

## 02-Air System Sizer
Absolute roughness - k - for some common materials
[17 empty] | Fluid density (kg/m3) |  | 1.204 |  | Galvanised steel |  | 0.15 | mm
[17 empty] | Duct material |  | Galvanised steel |  | Flexible duct |  | 1 | mm
[17 empty] | Abs. roughness (mm) |  | 0.15 |  | Lagged duct |  | 0.375 | mm
System: | XXX
Level | Room/Grille Type 1 |  |  |  | Room/Grille Type 2 |  |  |  | Room/Grille Type 3 |  |  |  | Room/Grille Type 4 |  |  |  | Total Flow | Duct Branch Sizer | [7 empty] | Total Flow | Duct Riser Sizer | [7 empty] | Nos. of Grille | Air Flow | Grille Sizer
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | Width | Height | Face Velocity | ε | Dh | Re | Fd | Fric Loss |  | Width | Height | Face Velocity | ε | Dh | Re | Fd | Fric Loss |  |  | Width | Height | Area Ratio | Face velocity | Act, Velocity
| Room/Grille Type 1 Rate: L/s; Room/Grille Type 1 Flow: L/s; Room/Grille Type 2 Rate: L/s; Room/Grille Type 2 Flow: L/s; Room/Grille Type 3 Rate: L/s; Room/Grille Type 3 Flow: L/s; Room/Grille Type 4 Rate: L/s; Room/Grille Type 4 Flow: L/s | L/s | m | m | m/s | mm | mm |  |  | Pa/m | L/s | m | m | m/s | mm | mm |  |  | Pa/m |  | L/s | m | m | % | m/s | m/s
XXX | Room/Grille Type 1 NO.: 1; Room/Grille Type 1 Rate: 2300; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [25 empty] | Shop 301
| Room/Grille Type 1 Flow: 2300; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 2300 | 0.95 | 0.35 | 6.9173 | 0.15 | 511.5385 | 234953.8462 | 0.017434 | 0.98174 |  |  |  | - | [5 empty] | 1 | 181 | 1.2 | 0.15 | 60% | 1.0056 | 1.6759 |  | 4300Wx1200D
| Room/Grille Type 1 NO.: 0; Room/Grille Type 1 Rate: 0; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [25 empty] | Hood-1 |  | Designed Air Flow,L/s |  | 2140
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 2 | 0 | 0 | 0 | 50% | - | - | NO. | Fliter | Size X, mm | Size Y, mm | Velocity point 1 | Velocity point 2 | Velocity point 3 | Velocity point 4 | Velocity point 5 | Air Flow, L/s
| Room/Grille Type 1 NO.: 0; Room/Grille Type 1 Rate: 0; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [25 empty] | 1 | SS Filter | 410 | 340 | 3.9 | 4 | 3.9 | 3.9 | 3.9 | 546.448
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | - | 2 | SS Filter | 410 | 340 | 4.2 | 4.5 | 4 | 3.9 | 3.9 | 571.54
| Room/Grille Type 1 NO.: 0; Room/Grille Type 1 Rate: 0; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [25 empty] | 3 | SS Filter | 410 | 340 | 5.1 | 4.1 | 4.2 | 4 | 3.5 | 582.692
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | - | 4 | SS Filter | 410 | 340 | 4.2 | 4.5 | 4.2 | 3.7 | 4.7 | 593.844
| Room/Grille Type 1 NO.: 0; Room/Grille Type 1 Rate: 0; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [25 empty] | 5 | SS Filter | 410 | 340 | 3.2 | 3.2 | 3.5 | 2.8 | 2.9 | 434.928
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | - | 6 | SS Filter | 410 | 340 | 5 | 4.5 | 4.6 | 4.7 | 4.3 | 644.028
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | - | [6 empty] | Designed Air Flow,L/s | 1220 | Total | 3373.48
| Room/Grille Type 1 NO.: 0; Room/Grille Type 1 Rate: 0; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [33 empty] | Percentage, % | 276.5%
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| Room/Grille Type 1 NO.: 0; Room/Grille Type 1 Rate: 0; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0 | [25 empty] | Shop 302
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | - |  | 2300Wx1150D
[42 empty] | Hood-1 |  | Designed Air Flow,L/s |  | 1160
[42 empty] | NO. | Fliter | Size X, mm | Size Y, mm | Velocity point 1 | Velocity point 2 | Velocity point 3 | Velocity point 4 | Velocity point 5 | Air Flow, L/s
[42 empty] | 1 | SS Filter | 410 | 340 | 1.4 | 1.3 | 1.3 |  |  | 185.8667
[42 empty] | 2 | SS Filter | 410 | 340 | 2 | 1.7 | 1.3 |  |  | 232.3333
[42 empty] | 3 | SS Filter | 410 | 340 | 1.5 | 1.6 | 1.4 |  |  | 209.1
[42 empty] | 4 | SS Filter | 410 | 340 | 1.2 | 1.4 | 1.3 |  |  | 181.22
[48 empty] | Designed Air Flow,L/s | 1210 | Total | 808.52
[50 empty] | Percentage, % | 66.82%
2300Wx1150D
[42 empty] | Hood-2 |  | Designed Air Flow,L/s |  | 1120
[42 empty] | NO. | Fliter | Size X, mm | Size Y, mm | Velocity point 1 | Velocity point 2 | Velocity point 3 | Velocity point 4 | Velocity point 5 | Air Flow, L/s
[42 empty] | 1 | SS Filter | 410 | 340 | 1.2 | 1.1 | 1.1 |  |  | 157.9867
[42 empty] | 2 | SS Filter | 410 | 340 | 1.2 | 1.2 | 1 |  |  | 157.9867
[42 empty] | 3 | SS Filter | 410 | 340 | 1.8 | 1.6 | 1.2 |  |  | 213.7467
[42 empty] | 4 | SS Filter | 410 | 340 | 2 | 1.8 | 1.4 |  |  | 241.6267
[48 empty] | Designed Air Flow,L/s | 720 | Total | 771.3467
[50 empty] | Percentage, % | 107.1%
1000Wx1000D
[42 empty] | Dishwasher hood |  | Designed Air Flow,L/s |  | 300
[42 empty] | NO. | Fliter | Size X, mm | Size Y, mm | Velocity point 1 | Velocity point 2 | Velocity point 3 | Velocity point 4 | Velocity point 5 | Air Flow, L/s
[42 empty] | 1 | No filter | 240 | 240 | 5 |  |  |  |  | 288
[42 empty] | 2 | [8 empty] | 0
[42 empty] | 3 | [8 empty] | 0
[48 empty] | Designed Air Flow,L/s | 300 | Total | 288
[50 empty] | Percentage, % | 96%
Note on W7: Freeman J: Material absolute roughness factor (mm) - ε
Note on X7: Freeman J: Hydraulic diameter (mm) - Dh
Note on Y7: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on Z7: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AA7: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AG7: Freeman J: Material absolute roughness factor (mm) - ε
Note on AH7: Freeman J: Hydraulic diameter (mm) - Dh
Note on AI7: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AJ7: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AK7: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation

## 03-Ventilation Rate
Room Name | Type | Area | Load rate | Air flow
|  | m2 | W/m2 | L/s
50
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Examples
Toilet | Exhaust | 8 | 10 | 80
Gabage room | Exhaust | 10 | 5 | 100
Grease Arrestor | Exhaust | 15 | 5 | 100
Plant room | Exhaust/Supply | 15 | 5 | 100
Main Switch room | Supply | 15 | 5 | 75
Distribuiotn Borad room | Supply | 15 | 5 | 75
Stoage | Supply | 10 | 5 | 50
Lobby/Corridor | Supply | 55 | 1 | 55

## 04-Exhaust Hood
[18 empty] | Fluid density (kg/m3) |  | 1.204
[18 empty] | Duct material |  | Galvanised steel
[18 empty] | Abs. roughness (mm) |  | 0.15
Absolute roughness - k - for some common materials
[18 empty] | Galvanised steel |  | 0.15 | mm
[18 empty] | Flexible duct |  | 0.3 | mm
[18 empty] | Lagged duct |  | 0.375 | mm
[18 empty] | Ordinary concrete |  | 1 | mm
[18 empty] | Coarse concrete |  | 5 | mm
[18 empty] | Stainless steel |  | 0.006 | mm
[6 empty] | Type 1-4 = | 150mm overhange
[6 empty] | Type 5 = | 300mm overhange
[6 empty] | Type 6 = | 600mm overhange
[6 empty] | Type 7 = | 450mm overhange
[9 empty] | Duct Sizer | [7 empty] | Dropper Qty | Air Flow | KE Dropper/ MA Flex Sizer | [7 empty] | REF. | Air Flow | Grille Sizer
[9 empty] | X | Y | Actu, Velocity | ε (mm) | Dh(mm) | Re | Fd | Fric Loss |  |  | X or Dia | Y | Actu, Velocity | ε (mm) | Dh(mm) | Re | Fd | Fric Loss |  |  | X | Y | Area Ratio | Face velocity | Act, Velocity |  |  | METAL Duct Sizer | [9 empty] | METAL Duct Sizer
[9 empty] | m | m | m/s | mm | mm |  |  | Pa/m |  | L/s | m | m | m/s | mm | mm |  |  | Pa/m |  | L/s | m | m | % | m/s | m/s |  |  | ID | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss | ID | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss
NO. | Hood Type | Cook Type | Vf | L | P | H | Q | [29 empty] | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m
1 | 3 | 6 | 320 |  | 4.2 | 1.1 | 1478.4 |  | 0.65 | 0.35 | 6.4985 | 0.15 | 455 | 196331.52 | 0.018009 | 1.0062 | 2 | 739.2 | 0.45 | 0.3 | 5.4756 | 0.15 | 360 | 130887.68 | 0.019362 | 0.97072 |  | 1478.4 | 0.9 | 0.85 | 50% | 1.9325 | 3.8651 |  |  | 1 | 85 | 0.2 | 0.2 | 2.125 | 0.15 | 200 | 28220 | 0.025784 | 0.35046 | 1 | 75 | 0.2 | 0.2 | 1.875 | 0.15 | 200 | 24900 | 0.026401 | 0.27937
[8 empty] | 1256.64 |  |  | - | 0.15 | - | - | - | - | 4 | 314.16 | 0.35 |  | 3.2607 | 1 | 350 | 75779.5804 | 0.027819 | 0.50875 |  | 1256.64 | [7 empty] | 2 | 170 | 0.2 | 0.2 | 4.25 | 0.15 | 200 | 56440 | 0.02302 | 1.2515 | 2 | 150 | 0.2 | 0.2 | 3.75 | 0.15 | 200 | 49800 | 0.023445 | 0.99237
[7 empty] | 0 |  | 0 | 0 | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 3 | 255 | 0.4 | 0.2 | 3.1875 | 0.15 | 266.6667 | 56440 | 0.022393 | 0.51362 | 3 | 225 | 0.4 | 0.2 | 2.8125 | 0.15 | 266.6667 | 49800 | 0.022845 | 0.40795
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0 | [7 empty] | 4 | 340 | 0.4 | 0.2 | 4.25 | 0.15 | 266.6667 | 75253.3333 | 0.021463 | 0.87519 | 4 | 300 | 0.4 | 0.2 | 3.75 | 0.15 | 266.6667 | 66400 | 0.02185 | 0.69365
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 5 | 425 | 0.4 | 0.2 | 5.3125 | 0.15 | 266.6667 | 94066.6667 | 0.020838 | 1.3277 | 5 | 375 | 0.4 | 0.2 | 4.6875 | 0.15 | 266.6667 | 83000 | 0.021179 | 1.0506
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0 | [7 empty] | 6 | 510 | 0.5 | 0.3 | 3.4 | 0.15 | 375 | 84660 | 0.020452 | 0.37954 | 6 | 450 | 0.5 | 0.3 | 3 | 0.15 | 375 | 74700 | 0.020843 | 0.30114
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 7 | 595 | 0.5 | 0.3 | 3.9667 | 0.15 | 375 | 98770 | 0.020005 | 0.5053 | 7 | 525 | 0.5 | 0.3 | 3.5 | 0.15 | 375 | 87150 | 0.020365 | 0.40049
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0 | [7 empty] | 8 | 680 | 0.5 | 0.3 | 4.5333 | 0.15 | 375 | 112880 | 0.019646 | 0.64815 | 8 | 600 | 0.5 | 0.3 | 4 | 0.15 | 375 | 99600 | 0.019981 | 0.51323
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 9 | 765 | 0.5 | 0.3 | 5.1 | 0.15 | 375 | 126990 | 0.019351 | 0.80801 | 9 | 675 | 0.5 | 0.3 | 4.5 | 0.15 | 375 | 112050 | 0.019665 | 0.63928
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0 | [7 empty] | 10 | 850 | 0.5 | 0.3 | 5.6667 | 0.15 | 375 | 141100 | 0.019104 | 0.98478 | 10 | 750 | 0.5 | 0.3 | 5 | 0.15 | 375 | 124500 | 0.019399 | 0.77856
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 11 | 935 | 0.7 | 0.3 | 4.4524 | 0.15 | 420 | 124168 | 0.019192 | 0.54531 | 11 | 825 | 0.7 | 0.3 | 3.9286 | 0.15 | 420 | 109560 | 0.019519 | 0.43179
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0 | [7 empty] | 12 | 1020 | 0.7 | 0.3 | 4.8571 | 0.15 | 420 | 135456 | 0.018977 | 0.64171 | 12 | 900 | 0.7 | 0.3 | 4.2857 | 0.15 | 420 | 119520 | 0.019289 | 0.50781
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 13 | 1105 | 0.7 | 0.3 | 5.2619 | 0.15 | 420 | 146744 | 0.018789 | 0.74565 | 13 | 975 | 0.7 | 0.3 | 4.6429 | 0.15 | 420 | 129480 | 0.019087 | 0.58974
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0 | [7 empty] | 14 | 1190 | 0.7 | 0.3 | 5.6667 | 0.15 | 420 | 158032 | 0.018622 | 0.85709 | 14 | 1050 | 0.7 | 0.3 | 5 | 0.15 | 420 | 139440 | 0.018908 | 0.67753
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | - |  |  | 15 | 1275 | 0.7 | 0.3 | 6.0714 | 0.15 | 420 | 169320 | 0.018473 | 0.97603 | 15 | 1125 | 0.7 | 0.3 | 5.3571 | 0.15 | 420 | 149400 | 0.018748 | 0.77119
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - | [11 empty] | 0 | [7 empty] | 16 | 1360 | 0.7 | 0.3 | 6.4762 | 0.15 | 420 | 180608 | 0.018339 | 1.1024 | 16 | 1200 | 0.7 | 0.3 | 5.7143 | 0.15 | 420 | 159360 | 0.018604 | 0.8707
[36 empty] | 17 | 1445 | 0.7 | 0.3 | 6.881 | 0.15 | 420 | 191896 | 0.018218 | 1.2363 | 17 | 1275 | 0.7 | 0.3 | 6.0714 | 0.15 | 420 | 169320 | 0.018473 | 0.97603
[6 empty] | Exhaust∑ | 1478.4 |  | 1 | 1 | 1.4784 | 0.15 | 1000 | 98165.76 | 0.01879 | 0.024723 | [10 empty] | Main Exhaust Grille | 1478.4 | 0 | 0 | 50% | - | - |  |  | 18 | 1530 | 0.7 | 0.3 | 7.2857 | 0.15 | 420 | 203184 | 0.018107 | 1.3777 | 18 | 1350 | 0.7 | 0.3 | 6.4286 | 0.15 | 420 | 179280 | 0.018354 | 1.0872
[6 empty] | Makeup∑ |  | 1256.64 | 0 | 0 | - | 0.15 | - | - | - | - | [10 empty] | Main Supply Grille | 1256.64 | 0 | 0 | 50% | - | - |  |  | 19 | 1615 |  |  | - | 0.15 | - | - | - | - | 19 | 1425 |  |  | - | 0.15 | - | - | - | -
[36 empty] | 20 | 1700 |  |  | - | 0.15 | - | - | - | - | 20 | 1500 |  |  | - | 0.15 | - | - | - | -
[36 empty] | 21 | 1785 |  |  | - | 0.15 | - | - | - | - | 21 | 1575 |  |  | - | 0.15 | - | - | - | -
[17 empty] | METAL Duct Sizer | [9 empty] | FLEX Duct Sizer | [8 empty] | 22 | 1870 |  |  | - | 0.15 | - | - | - | - | 22 | 1650 |  |  | - | 0.15 | - | - | - | -
[17 empty] | ID | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss | ID | Flow rate | Flex size | Velocity | ε | Dh | Re | Fd | Fric Loss | 23 | 1955 |  |  | - | 0.15 | - | - | - | - | 23 | 1725 |  |  | - | 0.15 | - | - | - | -
[18 empty] | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | Dia/m | m/s | mm | mm |  |  | Pa/m | 24 | 2040 |  |  | - | 0.15 | - | - | - | - | 24 | 1800 |  |  | - | 0.15 | - | - | - | -
[18 empty] | 1350 | 0.7 | 0.3 | 6.4286 | 0.15 | 420 | 179280 | 0.018354 | 1.0872 |  |  |  | - | 1 | 0 | - | - | - | 25 | 2125 |  |  | - | 0.15 | - | - | - | - | 25 | 1875 |  |  | - | 0.15 | - | - | - | -
[21 empty] | - | 0.15 | - | - | - | - |  |  |  | - | 1 | 0 | - | - | - | 26 | 2210 |  |  | - | 0.15 | - | - | - | - | 26 | 1950 |  |  | - | 0.15 | - | - | - | -
[18 empty] | 225 | 0.2 | 0.2 | 5.625 | 0.15 | 200 | 74700 | 0.022173 | 2.1117 |  |  |  | - | 1 | 0 | - | - | -
[21 empty] | - | 0.15 | - | - | - | - |  |  |  | - | 1 | 0 | - | - | -
[21 empty] | - | 0.15 | - | - | - | - |  |  |  | - | 1 | 0 | - | - | -
[21 empty] | - | 0.15 | - | - | - | - |  |  |  | - | 1 | 0 | - | - | -
[21 empty] | - | 0.15 | - | - | - | - |  |  |  | - | 1 | 0 | - | - | -
[21 empty] | - | 0.15 | - | - | - | - |  |  |  | - | 1 | 0 | - | - | -
[21 empty] | - | 0.15 | - | - | - | -
[21 empty] | - | 0.15 | - | - | - | -
[9 empty] | Duct Sizer | [7 empty] | Dropper Qty | Air Flow | KE Dropper/ MA Flex Sizer | [7 empty] | REF. | Air Flow | Grille Sizer
[9 empty] | X | Y | Actu, Velocity | ε (mm) | Dh(mm) | Re | Fd | Fric Loss |  |  | X or Dia | Y | Actu, Velocity | ε (mm) | Dh(mm) | Re | Fd | Fric Loss |  |  | X | Y | Area Ratio | Face velocity | Act, Velocity
[9 empty] | m | m | m/s | mm | mm |  |  | Pa/m |  | L/s | m | m | m/s | mm | mm |  |  | Pa/m |  | L/s | m | m | % | m/s | m/s
NO. | Hood Type | Cook Type | Vf | L | P | H | Q
1 | 2 | 4 | 375 |  | 3 | 1.1 | 1237.5 |  | 0.85 | 0.4 | 3.6397 | 0.15 | 544 | 131472 | 0.018615 | 0.27289 | 2 | 618.75 | 0.45 | 0.4 | 3.4375 | 0.15 | 423.5294 | 96670.5882 | 0.019855 | 0.33348 |  | 1237.5 | 0 | 0 | 50% | - | -
[8 empty] | 1051.875 |  |  | - | 0.15 | - | - | - | - | 4 | 262.9688 | 0.35 |  | 2.7294 | 1 | 350 | 63431.5684 | 0.02814 | 0.36057 |  | 1051.875
[7 empty] | 0 |  | 0 | 0 | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 1 | 0 | - | - | - |  | 0
[7 empty] | 0 |  |  |  | - | 0.15 | - | - | - | - |  | - |  |  | - | 0.15 | - | - | - | - |  | 0 | 0 | 0 | 50% | - | -
[8 empty] | 0 |  |  | - | 0.15 | - | - | - | - | [11 empty] | 0
[6 empty] | Exhaust∑ | 1237.5 |  | 1 | 1 | 1.2375 | 0.15 | 1000 | 82170 | 0.0194 | 0.017885 | [10 empty] | Main Exhaust Grille | 1237.5 | 0 | 0 | 50% | - | -
[6 empty] | Makeup∑ |  | 1051.875 | 0 | 0 | - | 0.15 | - | - | - | - | [10 empty] | Main Supply Grille | 1051.875 | 0 | 0 | 50% | - | -
Note on N23: Freeman J: Material absolute roughness factor (mm) - ε
Note on O23: Freeman J: Hydraulic diameter (mm) - Dh
Note on P23: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on Q23: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on R23: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Y23: Freeman J: Material absolute roughness factor (mm) - ε
Note on Z23: Freeman J: Hydraulic diameter (mm) - Dh
Note on AA23: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AB23: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AC23: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AT24: Freeman J: Material absolute roughness factor (mm) - ε
Note on AU24: Freeman J: Hydraulic diameter (mm) - Dh
Note on AV24: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AW24: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AX24: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on BE24: Freeman J: Material absolute roughness factor (mm) - ε
Note on BF24: Freeman J: Hydraulic diameter (mm) - Dh
Note on BG24: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on BH24: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on BI24: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Y48: Freeman J: Material absolute roughness factor (mm) - ε
Note on Z48: Freeman J: Hydraulic diameter (mm) - Dh
Note on AA48: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AB48: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AC48: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AI48: Freeman J: Material absolute roughness factor (mm) - ε
Note on AJ48: Freeman J: Hydraulic diameter (mm) - Dh
Note on AK48: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AL48: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AM48: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on N67: Freeman J: Material absolute roughness factor (mm) - ε
Note on O67: Freeman J: Hydraulic diameter (mm) - Dh
Note on P67: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on Q67: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on R67: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Y67: Freeman J: Material absolute roughness factor (mm) - ε
Note on Z67: Freeman J: Hydraulic diameter (mm) - Dh
Note on AA67: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AB67: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AC67: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation

## 05-Design Checklist
Project Number
Project Name
DESIGN CHECKLIST
No. | Checking Items | First Check |  |  |  | Second Check |  | Final Check
|  | By whom | XXX | Date | XXXX | By whom | Date | By whom | Date
Initial setup / Drawing template
1.1 | Used right drawing template? A3 or A1, Restaurant or Office, Class 2 or other class? | Y/N
1.2 | The tenancy location shown on drawings are mathc in google map, satellite photos snapshot taken?
1.3 | The project name is not too long? Is the shop name put on?
1.4 | Get right project number?
1.5 | Drawing size correct? Scale is 1:100 or 1:50?
1.6 | Kitchen ventilation scope, table top BBQ(dropper or exhaust at low level), horizontal discharge, KE riser provision, Charcoal, etc
1.7 | AC is in the scope of work?
1.8 | Need roof layout?
Arch/Mech Drawings Setup
2.1 | The tenancy location shown on drawings are mathc in google map, satellite photos snapshot taken?
2.2 | The project name is not too long? Is the shop name put on?
2.3 | The tenancy address on google map are match project name?
2.4 | Search tenacy phoho on internet, snapshot/save in the photo folder for reference, how may photos available? Inside, outside, roof?
2.5 | Check is there any Existing Mechanical drwings with any existing mechanical system provided by clients?
2.6 | Existing Mechanical drwings put into mech drawings and sketch out properly?
2.7 | Check is there any photo provided by clients? Put important one in the drawings
2.8 | Check is there any 360 photo we taken? Put important one in the drawings with doc's name
Kitchen Design
3.1 | Did all the kitchen equipment schedule are snap shot and put in the drawings
3.2 | Dishwasher in the tenancy, what type, underbench dishwasher? commercial dishwasher need hood? Hoodless type commercial dishwasher?
3.2 | Check kitchen hood(s) size, correct overhang with right type of cooking?
3.3 | Check the calculation of kitchen make up and exhaust air flow for hoods are corrects?
3.4 | Check kitchen make up and exhaust air flow for any ductworks, diffusers, flexable ducts and dropper size are corrects?
3.5 | Check kitchen make up air and exhaust air fans air flow are correct? Descriptions correct?
3.6 | Type of ceiling: Plasterboard, T bar, Open ceiling or featured ceiling, provided Access panel for fan and exhaust duct ?
3.7 | Check all the description are correct ?
A/C Design
4.1 | AC is in the scope of work?
4.2 | Area calculation done? Check the AC load estimation w/sqm are within the range
4.3 | Mechanical outside air or natural ventilation?
4.4 | AC TYPE, PAC, SPILT OR VRV?
4.5 | AC grilles design matching the architect RCP drawings?
4.6 | A/C supply type: 4 way blow diffuser, linear bar grille or linear slot diffuser (?? slots)? Air flow match AC load calculation? Size correct?
4.7 | A/C Return type: open ceiling, Egg crate grille or linar bar grille? size correctly?
4.8 | Outside air flow to each FCU shown? match AC load calcualtion?
4.9 | The total supply Air Flow on grilles match FCU supply air?
4.1 | Condensate Drain pipe and Tundish provided in drawing? Drain pipe sized correctly?
4.11 | Access panel for FCU, Fan shown?
4.12 | AC pipe type: Refrigeration pipe, Chiller water pipe or condensing water pipe, sized correctly? Connection schemtic/details shown?
4.13 | Check all the description are correct ?
Prior Issue
5.1 | Type of issued? For construction? For Approve? For As-built? etc.
5.2 | Drawing number Correct?
5.3 | Date correct?
5.4 | Used latest version Background? Flatten correctly?
5.5 | One more time to Check all the description are correct?
5.6 | Drawing list updated in fee proposal excel?

## Casual Duct Sizer
Absolute roughness - k - for some common materials
[12 empty] | Fluid density (kg/m3) |  | 1.204 |  | Galvanised steel | 0.15 | mm
[12 empty] | Duct material |  | Flexible duct |  | Flexible duct | 0.3 | mm
[12 empty] | Abs. roughness (mm) |  | 0.3 |  | Lagged duct | 0.375 | mm
[16 empty] | Ordinary concrete | 1 | mm
[16 empty] | Coarse concrete | 5 | mm
[16 empty] | Stainless steel | 0.006 | mm
METAL Duct Sizer | [9 empty] | MASONRY Duct Sizer | [9 empty] | FLEX Duct Sizer | [8 empty] | GRILLE Sizer
| Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Flex size | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Grille size |  | % | Face velocity | Act, Velocity
| L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | Dia/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m |  | m/s | m/s
1 | 50 | 0.2 | 0.15 | 1.6667 | 0.15 | 171.4286 | 18971.4286 | 0.028149 | 0.27458 | 1 | 5000 | 0.8 | 0.8 | 7.8125 | 1 | 800 | 415000 | 0.021489 | 0.98695 | 1 | 300 | 0.3 | 4.2382 | 1 | 300 | 84424.6662 | 0.028654 | 1.0328 | 1 | 100 | 0.4 | 0.4 | 50% | 0.625 | 1.25
2 |  |  |  | - | 0.15 | - | - | - | - | 2 |  |  |  | - | 1 | - | - | - | - | 2 |  |  | - | 1 | 0 | - | - | - | 2 |  |  |  |  | - | -
3 |  |  |  | - | 0.15 | - | - | - | - | 3 |  |  |  | - | 1 | - | - | - | - | 3 |  |  | - | 1 | 0 | - | - | - | 3 |  |  |  |  | - | -
4 |  |  |  | - | 0.15 | - | - | - | - | 4 |  |  |  | - | 1 | - | - | - | - | 4 |  |  | - | 1 | 0 | - | - | - | 4 |  |  |  |  | - | -
5 |  |  |  | - | 0.15 | - | - | - | - | 5 |  |  |  | - | 1 | - | - | - | - | 5 |  |  | - | 1 | 0 | - | - | - | 5 |  |  |  |  | - | -
6 |  |  |  | - | 0.15 | - | - | - | - | 6 |  |  |  | - | 1 | - | - | - | - | 6 |  |  | - | 1 | 0 | - | - | - | 6 |  |  |  |  | - | -
7 |  |  |  | - | 0.15 | - | - | - | - | 7 |  |  |  | - | 1 | - | - | - | - | 7 |  |  | - | 1 | 0 | - | - | - | 7 |  |  |  |  | - | -
8 |  |  |  | - | 0.15 | - | - | - | - | 8 |  |  |  | - | 1 | - | - | - | - | 8 |  |  | - | 1 | 0 | - | - | - | 8 |  |  |  |  | - | -
METAL Duct Size Table | [9 empty] | MASONRY Duct Size Table | [9 empty] | FLEX Duct Size Table | [8 empty] | GRILLE Size
| Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Flex size | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Grille size |  | % | Face velocity | Act, Velocity
| L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | Dia/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m |  | m/s | m/s
1 | 100 | 0.25 | 0.15 | 2.6667 | 0.15 | 187.5 | 33200 | 0.025175 | 0.57478 | 1 | 200 | 0.25 | 0.25 | 3.2 | 1 | 250 | 53120 | 0.030708 | 0.75718 | 1 | 55 | 0.15 | 3.108 | 1 | 150 | 30955.711 | 0.036037 | 1.397 | 1 | 20 | 0.15 | 0.15 | 50% | 0.88889 | 1.7778
2 | 200 | 0.4 | 0.15 | 3.3333 | 0.15 | 218.1818 | 48290.9091 | 0.02336 | 0.71616 | 2 | 500 | 0.35 | 0.35 | 4.0816 | 1 | 350 | 94857.1429 | 0.027473 | 0.78724 | 2 | 120 | 0.2 | 3.8144 | 1 | 200 | 50654.7997 | 0.032509 | 1.4237 | 2 | 40 | 0.2 | 0.2 | 50% | 1 | 2
3 | 400 | 0.5 | 0.2 | 4 | 0.15 | 285.7143 | 75885.7143 | 0.021294 | 0.71785 | 3 | 1000 | 0.45 | 0.45 | 4.9383 | 1 | 450 | 147555.5556 | 0.025395 | 0.82849 | 3 | 195 | 0.25 | 3.9669 | 1 | 250 | 65851.2397 | 0.030327 | 1.1492 | 3 | 60 | 0.25 | 0.25 | 50% | 0.96 | 1.92
4 | 600 | 0.5 | 0.25 | 4.8 | 0.15 | 333.3333 | 106240 | 0.020036 | 0.83369 | 4 | 2000 | 0.6 | 0.6 | 5.5556 | 1 | 600 | 221333.3333 | 0.023406 | 0.7248 | 4 | 250 | 0.3 | 3.5318 | 1 | 300 | 70353.8885 | 0.028937 | 0.72431 | 4 | 70 | 0.3 | 0.3 | 50% | 0.77778 | 1.5556
5 | 800 | 0.6 | 0.25 | 5.3333 | 0.15 | 352.9412 | 124988.2353 | 0.019512 | 0.94668 | 5 | 5000 | 0.85 | 0.85 | 6.9204 | 1 | 850 | 390588.2353 | 0.021245 | 0.72061 | 5 | 355 | 0.35 | 3.6846 | 1 | 350 | 85630.7329 | 0.027623 | 0.64505 | 5 | 80 | 0.3 | 0.3 | 50% | 0.88889 | 1.7778
6 | 1000 | 0.8 | 0.25 | 5 | 0.15 | 380.9524 | 126476.1905 | 0.01933 | 0.76366 | 6 | 10000 | 1.1 | 1.1 | 8.2645 | 1 | 1100 | 603636.3636 | 0.019835 | 0.74142 | 6 | 500 | 0.4 | 3.9733 | 1 | 400 | 105530.8328 | 0.026503 | 0.6297 | 6 | 90 | 0.35 | 0.35 | 50% | 0.73469 | 1.4694
7 | 1500 | 1 | 0.3 | 5 | 0.15 | 461.5385 | 153230.7692 | 0.018513 | 0.60368 | 7 | 15000 | 1.25 | 1.25 | 9.6 | 1 | 1250 | 796800 | 0.01916 | 0.85042 | 7 | 600 | 0.45 | 3.7673 | 1 | 450 | 112566.2217 | 0.025731 | 0.48853 | 7 | 100 | 0.4 | 0.4 | 50% | 0.625 | 1.25
8 | 2000 | 1.2 | 0.3 | 5.5556 | 0.15 | 480 | 177066.6667 | 0.01812 | 0.70139 | 8 | 20000 | 1.4 | 1.4 | 10.2041 | 1 | 1400 | 948571.4286 | 0.018627 | 0.83399 | 8 | [8 empty] | 8 | 120 | 0.4 | 0.4 | 50% | 0.75 | 1.5
Note on F14: Freeman J: Material absolute roughness factor (mm) - ε
Note on G14: Freeman J: Hydraulic diameter (mm) - Dh
Note on H14: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on I14: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on J14: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Q14: Freeman J: Material absolute roughness factor (mm) - ε
Note on R14: Freeman J: Hydraulic diameter (mm) - Dh
Note on S14: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on T14: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on U14: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AA14: Freeman J: Material absolute roughness factor (mm) - ε
Note on AB14: Freeman J: Hydraulic diameter (mm) - Dh
Note on AC14: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AD14: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AE14: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on F34: Freeman J: Material absolute roughness factor (mm) - ε
Note on G34: Freeman J: Hydraulic diameter (mm) - Dh
Note on H34: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on I34: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on J34: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Q34: Freeman J: Material absolute roughness factor (mm) - ε
Note on R34: Freeman J: Hydraulic diameter (mm) - Dh
Note on S34: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on T34: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on U34: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AA34: Freeman J: Material absolute roughness factor (mm) - ε
Note on AB34: Freeman J: Hydraulic diameter (mm) - Dh
Note on AC34: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AD34: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AE34: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation

## Casual Pipe Sizer
Chilled Water Pipe Sizer |  | Cooling/Condensate Water Pipe Sizer |  | Heating Hot Water Pipe Sizer |  | AC Condensate Water Pipe Sizer
Flow Rate | Diameter | Flow Rate | Diameter | Flow Rate | Diameter | Cooling Load | Diameter
2.25 | 65 | 14 | 100 | 0.01 | 15 | 44.5 | 32
3.51 | 80 | 14.01 | 125 | 0.04 | 20 | 100 | 40
5.8 | 80 | 14.1 | 125 | - | - | 101 | 40
- | - | 25 | 125 | - | - | - | -
- | - | - | - | - | - | - | - |  |  | Type | ID | Parameter | Lowest In Range | Highest In Range | Diameter
- | - | - | - | - | - | - | - |  |  |  |  | < L/s | L/s | L/s | mm
- | - | - | - | - | - | - | -
- | - | - | - | - | - | - | -
[10 empty] | Chilled water pipe size | chilled_water_pipe | 12.51 | 5.81 | 12.51 | 100
Chilled Water Pipe Size Lookup Table |  | Cooling/Condensate Water Pipe Lookup Table |  | Heating Hot Water Pipe Lookup Table |  | AC Condensate Water Pipe Lookup Table |  | Pipe Size Guide | Type ID | Chilled water pipe size | chilled_water_pipe | 23.01 | 12.51 | 23.01 | 125
Flowrate (l/s) | DN(mm) | Flowrate (l/s) | DN(mm) | Flowrate (l/s) | DN(mm) | Cooling Load (kW) | DN(mm) | Chilled | chilled_water_pipe | Chilled water pipe size | chilled_water_pipe | 38.01 | 23.01 | 38.01 | 150
0.04 | 15 | 0.04 | 15 | 0.04 | 15 | 7 | 20 | Hot Water | hot_water_pipe | Chilled water pipe size | chilled_water_pipe | 78.01 | 38.01 | 78.01 | 200
0.12 | 20 | 0.12 | 20 | 0.12 | 20 | 17.6 | 25 | Condenser Water | condenser_water_pipe | Chilled water pipe size | chilled_water_pipe | 121.1 | 78.01 | 121.1 | 250
0.26 | 25 | 0.28 | 25 | 0.31 | 25 | 100 | 32 |  |  | Chilled water pipe size | chilled_water_pipe | 173.1 | 121.1 | 173.1 | 300
0.51 | 32 | 0.56 | 32 | 0.61 | 32 | 176 | 40 |  |  | Chilled water pipe size | chilled_water_pipe | 209.1 | 173.1 | 209.1 | 350
0.81 | 40 | 0.91 | 40 | 1.01 | 40 | 598 | 50 |  |  | Chilled water pipe size | chilled_water_pipe | 273.1 | 209.1 | 273.1 | 400
2.01 | 50 | 2.11 | 50 | 2.26 | 50 | 1055 | 80 |  |  | Chilled water pipe size | chilled_water_pipe | 345.1 | 273.1 | 345.1 | 450
3.51 | 65 | 3.81 | 65 | 4.41 | 65 | 1512 | 100 |  |  | Chilled water pipe size | chilled_water_pipe | 430.1 | 345.1 | 430.1 | 500
5.81 | 80 | 6.26 | 80 | 7.01 | 80 | 12462 | 125 |  |  | Chilled water pipe size | chilled_water_pipe | 523.1 | 430.1 | 523.1 | 550
12.51 | 100 | 14.01 | 100 | 15.01 | 100 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0 | 0 | 0 | 0
23.01 | 125 | 25.01 | 125 | 27.01 | 125 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.04 | 1e-12 | 0.4 | 15
38.01 | 150 | 40.01 | 150 | 43.01 | 150 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.12 | 0.4 | 0.12 | 20
78.01 | 200 | 80.01 | 200 | 80.01 | 200 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.31 | 0.12 | 0.26 | 25
121.1 | 250 | 125.1 | 250 | 125.1 | 250 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.61 | 0.26 | 0.51 | 32
173.1 | 300 | 173.1 | 300 | 173.1 | 300 |  |  |  |  | Hot water pipe size | hot_water_pipe | 1.01 | 0.51 | 0.81 | 40
209.1 | 350 | 209.1 | 350 | 209.1 | 350 |  |  |  |  | Hot water pipe size | hot_water_pipe | 2.26 | 0.81 | 2.01 | 50
273.1 | 400 | 273.1 | 400 | 273.1 | 400 |  |  |  |  | Hot water pipe size | hot_water_pipe | 4.41 | 2.01 | 3.51 | 65
345.1 | 450 | 345.1 | 450 | 345.1 | 450 |  |  |  |  | Hot water pipe size | hot_water_pipe | 7.01 | 3.51 | 5.81 | 80
430.1 | 500 | 430.1 | 500 | 430.1 | 500 |  |  |  |  | Hot water pipe size | hot_water_pipe | 15.01 | 5.81 | 12.51 | 100
523.1 | 550 | 523.1 | 550 | 523.1 | 550 |  |  |  |  | Hot water pipe size | hot_water_pipe | 27.01 | 12.51 | 23.01 | 125
623 | 600 | 623 | 600 | 623 | 600 |  |  |  |  | Hot water pipe size | hot_water_pipe | 43.01 | 23.01 | 38.01 | 150
[10 empty] | Hot water pipe size | hot_water_pipe | 80.01 | 38.01 | 78.01 | 200
[10 empty] | Hot water pipe size | hot_water_pipe | 125.1 | 78.01 | 121.1 | 250
[10 empty] | Hot water pipe size | hot_water_pipe | 173.1 | 121.1 | 173.1 | 300
[10 empty] | Hot water pipe size | hot_water_pipe | 209.1 | 173.1 | 209.1 | 350
[10 empty] | Hot water pipe size | hot_water_pipe | 523.1 | 430.1 | 523.1 | 550
[10 empty] | Condenser water pipe size | condenser_water_pipe | 523.1 | 430.1 | 523.1 | 550
[10 empty] | Condenser water pipe size | condenser_water_pipe | 623 | 523.1 | 623 | 600

## REF (hidden)
Duct Length (m) - L | 6 | m
Duct Width (mm) - a | 500 | mm
Duct Height (mm) - b | 300 | mm
Hydraulic diameter (mm) - Dh | 375 | mm
Equivalent Diameter (mm) - De | 419.9793 | mm
Airflow (l/s) - Q | 735 | l/s
Airflow (m3/s) - Q | 0.735 | m3/s
Velocity (m/s) - v | 4.9 | m/s
Air density (kg/m3) - ρ | 1.204 | kg/m3
Material absolute roughness factor (mm) - ε | 0.15 | mm | Galvanized steel 0.15mm; Ordinary concrete 0.3-1mm
Reynolds Number | 122010 |  | ASHRAE Fundemental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Darcy–Weisbach friction factor - f (Swamee and Jain) | 0.019449 |  | Colebrook Equation Approximations
Darcy–Weisbach friction factor - f (Haaland) | 0.019126 |  |  | Swamee and Jain Equation (1976) | Haaland (1983) | Tsai（1989）
Darcy–Weisbach friction factor - f (Tsai) | 0.019349
Imperical friction loss (Pa/m) | 0.79254 | Pa/m
Calcualtion Method | Tsai |  | Imperical
Friction Loss (Pa/m) | 0.74579 | Pa/m | Swamee Jain
Friction Loss Section (Pa) -ΔP | 4.4747 | Pa | Haaland |  |  | Imperical
Tsai

## REF-AC Data
System | Type | CU/FCU | Model Number | Nominal Cooling Capacity(kW) | Nominal Heating Capacity(kW) | Nominal Air Flow (l/s) | Highest Air Flow (l/s)
SPC | Split Ducted Standard | FCU | FDYAN50AV1 | 5 | 6 | 370 | 370
SPC | Split Ducted Standard | FCU | FDYAN60AV1 | 6 | 7 | 400 | 400
SPC | Split Ducted Standard | FCU | FDYAN71AV1 | 7.1 | 7.5 | 566 | 566
SPC | Split Ducted Standard | FCU | FDYAN85AV1 | 8.5 | 10 | 600 | 600
SPC | Split Ducted Standard | FCU | FDYAN100AV1 | 10 | 12.5 | 800 | 800
SPC | Split Ducted Standard | FCU | FDYAN125AV1 | 12.5 | 15 | 840 | 840
SPC | Split Ducted Standard | FCU | FDYAN140AV1 | 14 | 16.5 | 1000 | 1000
SPC | Split Ducted Standard | FCU | FDYAN160AV1 | 15.5 | 18 | 1120 | 1120
SPC | Split Ducted Standard | FCU | FDYQN180LCV1 | 18 | 20 | 1200 | 1200
SPC | Split Ducted Standard | FCU | FDYQN200LCV1 | 19.5 | 22.4 | 1600 | 1600
SPC | Split Ducted Standard | FCU | FDYQN250LBV1 | 23.5 | 26.8 | 1600 | 1600
SPC | Split Ducted Low Profile | FCU | FBA50BAVMA | 5 | 6 | 300 | 300
SPC | Split Ducted Low Profile | FCU | FBA60BAVMA | 6 | 7.1 | 300 | 300
SPC | Split Ducted Low Profile | FCU | FBA71BVMA | 7.1 | 8 | 383 | 383
SPC | Split Ducted Low Profile | FCU | FBA85BVMA | 8.5 | 10 | 533 | 533
SPC | Split Ducted Low Profile | FCU | FBA100BVMA | 10 | 11.2 | 533 | 533
SPC | Split Ducted Low Profile | FCU | FBA125BVMA | 12.5 | 14 | 600 | 600
SPC | Split Ducted Low Profile | FCU | FBA140BVMA | 14 | 16 | 600 | 600
VRV | STANDARD DUCTED TYPE | FCU | FXMQ20PAVE | 2.2 | 2.5 | 150 | 150
VRV | STANDARD DUCTED TYPE | FCU | FXMQ25PAVE | 2.8 | 3.2 | 150 | 150
VRV | STANDARD DUCTED TYPE | FCU | FXMQ32PAVE | 3.6 | 4 | 158 | 158
VRV | STANDARD DUCTED TYPE | FCU | FXMQ40PAVE | 4.5 | 5 | 267 | 267
VRV | STANDARD DUCTED TYPE | FCU | FXMQ50PAVE | 5.6 | 6.3 | 300 | 300
VRV | STANDARD DUCTED TYPE | FCU | FXMQ63PAVE | 7.1 | 8 | 325 | 325
VRV | STANDARD DUCTED TYPE | FCU | FXMQ80PAVE | 9 | 10 | 417 | 417
VRV | STANDARD DUCTED TYPE | FCU | FXMQ100PAVE | 11.2 | 12.5 | 533 | 533
VRV | STANDARD DUCTED TYPE | FCU | FXMQ125PAVE | 14 | 16 | 650 | 650
VRV | STANDARD DUCTED TYPE | FCU | FXMQ140PAVE | 16 | 18 | 767 | 767
VRV | STANDARD DUCTED TYPE | FCU | FXMQ160PV1A | 18 | 20 | 1120 | 1120
VRV | STANDARD DUCTED TYPE | FCU | FXMQ180PV1A | 20 | 22.4 | 1160 | 1160
VRV | STANDARD DUCTED TYPE | FCU | FXMQ200PV1A | 22.4 | 25 | 1200 | 1200
VRV | STANDARD DUCTED TYPE | FCU | FXMQ250PV1A | 28 | 31.5 | 1400 | 1400
VRV | WARDROBE TYPE | FCU | FXDQ20TV1B | 2.2 | 2.5 | 135 | 135
VRV | WARDROBE TYPE | FCU | FXDQ25TV1B | 2.8 | 3.2 | 150 | 150
VRV | WARDROBE TYPE | FCU | FXDQ32TV1B | 3.6 | 4 | 150 | 150
VRV | WARDROBE TYPE | FCU | FXDQ40TV1B | 4.5 | 5 | 210 | 210
VRV | WARDROBE TYPE | FCU | FXDQ50TV1B | 5.6 | 6.3 | 250 | 250
VRV | WARDROBE TYPE | FCU | FXDQ63TV1B | 7.1 | 8 | 333 | 333
PLEASE SELECT
VRV | VRV IV S | CU | RXYMQ3AV4A | 9 | 10
VRV | VRV IV S | CU | RXYMQ4AV4A | 11.2 | 12.5
VRV | VRV IV S | CU | RXYMQ5AV4A | 14 | 14
VRV | VRV IV S | CU | RXYMQ6AV4A | 16 | 16
VRV | VRV IV S | CU | RXYMQ8AV4A | 22.4 | 22.4
VRV | VRV IV S | CU | RXYMQ9AV4A | 24 | 24
PLEASE SELECT

## Ver.
Revision | Date | Created by | Reviewed by | Description
1.0 | prior to 2022 | Felix Y |  | PCE original template
1.1 | 2022-01-06 | Freeman J | Felix Y | 'Exhaust Hood' friction loss calculation added
1.2 | 2022-01-06 | Freeman J |  | 'Duct System' friction loss calculation added
1.3 | 2022-01-27 | Felix Y
1.4 | 2022-02-03 | Chris P | Freeman J | To do: 1. 'AC Load' - add 'Split AC' selection and then check agaisnt room's AC load 2. 'AC Load' - add 'Duct system' and allocate air flow to each room 3. 'AC Load' - add CHW/HHW flow rate (if AC water system is designed) 4. One table per system (group of rooms) 5. 'Exhaust hood' - combine Dropper calculation into the main table 6. New Tab 'duct and griller sizer' - from separatre file (Felix) 7. 'Plantroom Vent' added. Fire pump room ventilation added 8. Added Pipe Sizing Calculator in '05-Pipe Sizing' 9. Quick Duct Sizing Chart added in '03-Air Duct Sizer' 10. REF - Daikin Equ Sch variables 11. REF- lookup chart variables
1.5 | 2022-02-14 | Freeman J | Felix Y | 01-AC Load - equipment/system auto-configuration added. REF-AC Data Sheet merged into 01-AC Load REF-Duct Size Chart added REF-Pipe Size Chart - AC Condensate pipe size chart added
1.6 | 2022-02-16 | Freeman J |  | 01-AC Load - simplfied calculation table REF-Duct Sizer - calculator added REF- Pipe Size Chart - quick lookup calculator added 04-Exhaust Hood - main exhaust and air intake grille size added
1.7 | 2022-03-03 | Chris | Freeman J | Made formatting the same, Calibri and size 10 Blue text for manual inputs Added E. Dh, Re,Fd and Fric Loss in duct sizer Did not add a calculator in duct sizer, wasn't too sure how you wanted it to be arranged Altered formula of pipe sizer to match each table Added in manual calculator, pipe sizer
1.8 | 2022-03-09 | Freeman J | Felix Y | Functionality Check
1.9 | 2022-03-11 | Freeman J |  | -Daikin AC Data Sheet listed in Separte Tab 'REF-DATA' -Wardrobe Type AC data added
2.0 | 2022-04-08 | Freeman J | Felix Y | Published
2.1 | 2022-06-09 | Freeman J |  | Pipe Sizer lookup tables updated
2.6 | 2024-02-26 | Felix Y |  | Adding Design Certificate, Design compliance cert
Table of Content
01 | AC Load Estimation
02 | Ventilation Rate
03 | Air Duct System Sizer
04 | Exhaust Hood Flow Rate
05 | Water System Sizer (to add)
06 | Fire Pump Plantroom Ventilation
07 | REF-Duct Size Chart
08 | REF-Pipe Size Chart
08 | REF-AC Data

## Sheet2 (hidden)
Level | Room Type 1 |  |  |  | Room Type 2 |  |  |  | Room Type 3 |  |  |  | Room Type4 |  |  |  | Room Type 5 |  |  |  | Room Type 6 |  |  |  | Room Type 7 |  |  |  | Room Type 8
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s; Room Type 6 Rate: L/s; Room Type 6 Flow: L/s; Room Type 7 Rate: L/s; Room Type 7 Flow: L/s; Room Type 8 Rate: L/s; Room Type 8 Flow: L/s | Rate | Flow
B1 | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 50; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 | L/s | L/s
|  |  |  | 50 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
G | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 30; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 |  | #REF!
|  |  |  | 30 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
L1 | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 30; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 |  | #REF!
|  |  |  | 30 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
L2 | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 30; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 |  | #REF!
|  |  |  | 30 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Room Type 2 Room: #REF!; Room Type 3 Room: #REF!; Room Type4 Room: #REF!; Room Type 5 Room: #REF!; Room Type 6 Room: #REF!; Room Type 7 Room: #REF!; Room Type 8 Room: #REF! |  | #REF!