## Duct System Sizer (hidden)
System: | CPEF
Level | Room Type 1 |  |  |  | Room Type 2 |  |  |  | Room Type 3 |  |  |  | Room Type4 |  |  |  | Room Type 5 |  |  |  | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s | Supply air | Exhaust 1 | Exhaust 2
B1 | Room Type 1 NO.: 6; Room Type 1 Rate: 400
| Room Type 1 Flow: 2400; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 2400 | 0.2 | 0.2 | 60 | 1920 | 1050 | 1950
G | Room Type 1 NO.: 2; Room Type 1 Rate: 450; Room Type 2 NO.: 4; Room Type 2 Rate: 450
| Room Type 1 Flow: 900; Room Type 2 Flow: 1800; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 2700 | 0 | 0 | #DIV/0! | 2160 | 945 | 1755
L1 | Room Type 1 NO.: 4; Room Type 1 Rate: 500; Room Type 2 NO.: 4; Room Type 2 Rate: 750
| Room Type 1 Flow: 2000; Room Type 2 Flow: 3000; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 5000 | 1.5 | 0.4 | 8.3333 | 4000 | 2000 | 3000
[21 empty] | 10100 | 1 | 1.8 | 5.6111 | 8080
[21 empty] | 10100 | 0.5 | 0.2 | 101
System: | Room Type 1 NO.: CPSF-2, S
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.5 | 0.3 | 0 | 672
G | Room Type 1 NO.: 5; Room Type 1 Rate: 152
| Room Type 1 Flow: 760; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 760 | 0 | 0 | #DIV/0! | 756
L1 | Room Type 1 NO.: 5; Room Type 1 Rate: 200
| Room Type 1 Flow: 1000; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1000 | 0 | 0 | #DIV/0! | 1400
[21 empty] | 1760 | 1 | 0.8 | 2.2 | 2828
[21 empty] | 1760 | 1.2 | 0.75 | 1.9556
System: | Room Type 1 NO.: CPSF-1, N
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1 | Room Type 1 NO.: 11; Room Type 1 Rate: 175
| Room Type 1 Flow: 1925; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1925 | 0.8 | 0.3 | 8.0208 | 1248
G | Room Type 1 NO.: 9; Room Type 1 Room: Ensuite; Room Type 1 Rate: 155
| Room Type 1 Flow: 1395; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1395 | 0.7 | 0.3 | 6.6429 | 1404
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.25 | 0.2 | 0 | 2600
[21 empty] | 3320 | 0.8 | 1 | 4.15 | 5252
[21 empty] | 3320 | 1 | 2 | 1.66
System: | Room Type 1 NO.: FPSF-1
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
G | Room Type 1 NO.: 2; Room Type 1 Rate: 750
| Room Type 1 Flow: 1500; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 1500 | 0.7 | 0.3 | 7.1429
[21 empty] | 1500 | 0.7 | 0.3 | 7.1429
[21 empty] | 1500 | 1.2 | 0.4 | 3.125
System: | Room Type 1 NO.: SAF-G-3
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
G | Room Type 1 NO.: 2; Room Type 1 Rate: 75
| Room Type 1 Flow: 150; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 150 | 0.7 | 0.3 | 0.71429
[21 empty] | 150 | 0.7 | 0.3 | 0.71429
[21 empty] | 150 | 1.2 | 0.4 | 0.3125
System: | Room Type 1 NO.: SAF-G-1
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G | Room Type 1 NO.: 2; Room Type 1 Room: Store; Room Type 1 Rate: 75
| Room Type 1 Flow: 150; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 150 | 0.2 | 0.2 | 3.75
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
[21 empty] | 150 | 0.4 | 0.2 | 1.875
System: | Room Type 1 NO.: SAF-G-2
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G | Room Type 1 NO.: 1; Room Type 1 Room: Store; Room Type 1 Rate: 15
| Room Type 1 Flow: 15; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 15 | 0.2 | 0.2 | 0.375
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.4 | 0.3 | 0
[21 empty] | 15 | 0.4 | 0.2 | 0.1875
System: | Room Type 1 NO.: GEF-R-1
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G | Room Type 1 NO.: 2; Room Type 1 Room: Garbage; Room Type 1 Rate: 120
| Room Type 1 Flow: 240; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 240 | 0.3 | 0.3 | 2.6667
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
[21 empty] | 240 | 0.25 | 0.25 | 3.84
System: | Room Type 1 NO.: TEF-R-6
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
L1 | Room Type 1 NO.: 5; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 200; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 200 | 0.2 | 0.2 | 5
L2 | Room Type 1 NO.: 5; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 200; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 200 | 0.2 | 0.2 | 5
[21 empty] | 400 | 0.3 | 0.2 | 6.6667
System: | Room Type 1 NO.: TEF-R-7
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1 | Room Type 1 NO.: 6; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 240; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 240 | 0.3 | 0.2 | 4
L2 | Room Type 1 NO.: 6; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 240; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 240 | 0.3 | 0.2 | 4
[21 empty] | 480 | 0.3 | 0.3 | 5.3333
System: | Room Type 1 NO.: TEF-R-8
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1 | Room Type 1 NO.: 2; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 80; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 80 | 0.2 | 0.15 | 2.6667
L2 | Room Type 1 NO.: 2; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 80; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 80 | 0.2 | 0.15 | 2.6667
[21 empty] | 160 | 0.2 | 0.2 | 4
System: | Room Type 1 NO.: TEF-R-9
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1 | Room Type 1 NO.: 4; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 160; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 160 | 0.2 | 0.2 | 4
L2 | Room Type 1 NO.: 4; Room Type 1 Room: Ensuite; Room Type 1 Rate: 40
| Room Type 1 Flow: 160; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 160 | 0.2 | 0.2 | 4
[21 empty] | 320 | 0.3 | 0.2 | 5.3333
System: | Room Type 1 NO.: GEF-B-2
Level | Room Type 1 NO.: Room Type 1; Room Type 2 NO.: Room Type 2; Room Type 3 NO.: Room Type 3; Room Type4 NO.: Room Type4; Room Type 5 NO.: Room Type 5 | Total Flow
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | X | Y | Actu, Velocity
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s | L/s | m | m | m/s
B1 | Room Type 1 NO.: 1; Room Type 1 Room: MSR; Room Type 1 Rate: 90
| Room Type 1 Flow: 90; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 90 |  |  | #DIV/0!
G
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0 | 0 | #DIV/0!
L1
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.2 | 0.2 | 0
L2
| Room Type 1 Flow: 0; Room Type 2 Flow: 0; Room Type 3 Flow: 0; Room Type4 Flow: 0; Room Type 5 Flow: 0 | 0 | 0.2 | 0.2 | 0
[21 empty] | 90 | 0.2 | 0.15 | 3
[21 empty] | 90 | 0.3 | 0.15 | 2

## Mechanical Design Certificate
Mechanical Design Certificate
Pursuant to the provisions of Clause A5.2 of the National Construction Code 2019 Admt 1, Volume 1. | [7 empty] | Pursuant to the provisions of Clause A5G3 of the National Construction Code 2022, Volume 1.
I | Qing Felix Ye |  | of | Premium Consulting Engineers
| (Appropriately qualified person) |  |  | (Firm)
Suite 802, 299 Sussex Street, Sydney NSW 2000
(Address)
Qualifications and experience:
Master of HVAC Engineering, Chartered Professional Engineer (MIEAust No.: 3631369);
NSW Fair Trading C9 Certifier (Reg No.: BDC04672); and
NSW Fair Trading Mechanical Design Practitioner (Reg No.: DEP0000275)
Hereby certify:
That the Mechanical Services Drawings and Specifications have been checked and comply with:
• | The relevant clauses of the National Construction Code 2019 Amendment 1. | [6 empty] | • | The relevant clauses of the National Construction Code 2022.
| BCA Clause |  | Description (Mechanical) | [5 empty] | BCA Clause | Description (Mechanical)
| Specification C1.10(5) |  | Fire Resistance Fire Hazard Property Air-handling ductwork | [5 empty] | Specification 7(S7C5) | Fire Resistance Fire Hazard Property Air-handling ductwork
| C1.10(5) |  | Fire Resistance Fire Hazard Property Air-handling ductwork | [5 empty] | C2D11 | Fire Resistance Fire Hazard Property Air-handling ductwork
| C3.9 |  | Fire Resistance Protection of openings Service penetrations in fire-isolated exits | [5 empty] | C4D10 | Fire Resistance Protection of openings Service penetrations in fire-isolated exits
| C3.12 |  | Fire resistance Protection of Openings Openings in floors and ceilings for services | [5 empty] | C4D13 | Fire resistance Protection of Openings Openings in floors and ceilings for services
| C3.15 |  | Fire resistance Protection of Openings Openings for service installations | [5 empty] | C4D15 | Fire resistance Protection of Openings Openings for service installations
| E2.2 (a), (b)& (c) |  | Smoke Hazard Management General requirements Air Handling Systems | [5 empty] | E2D3 | Smoke Hazard Management General requirements Air Handling Systems
| F4.5 |  | Health and Amenity Light and Ventilation Ventilation of rooms | [5 empty] | F6D6 | Health and Amenity Light and Ventilation Ventilation of rooms
| F4.6 |  | Health and amenity Light and ventilation Natural Ventilation | [5 empty] | F6D7 | Health and amenity Light and ventilation Natural Ventilation
| F4.11 |  | Health and Amenity Light and Ventilation Carparks | [5 empty] | F6D11 | Health and Amenity Light and Ventilation Carparks
| F4.12 |  | Health and Amenity Light and Ventilation Kitchen local exhaust ventilation | [5 empty] | F6D12 | Health and Amenity Light and Ventilation Kitchen local exhaust ventilation
| F6.3 |  | Health and amenity Condensation management Flow rate and discharge of exhaust systems | [5 empty] | F8D4 | Health and amenity Condensation management Flow rate and discharge of exhaust systems
| J3.5 |  | Energy Efficiency Building Sealing Exhaust Fans | [5 empty] | J5D6 | Health and amenity Condensation Management Ventilation of roof spaces
| J5 |  | Energy Efficiency Air-conditioning and Ventilation Systems | [5 empty] | J6 | Energy Efficiency Air-conditioning and Ventilation Systems
| NSW E2D16 |  | Automatic Shutdown
• | The referenced Australian Standards listed in the Building Code of Australia (Schedule 4 Referenced Documents) as follows:
| Standard |  | Description (Mechanical) | [5 empty] | Standard | Description (Mechanical)
| AS1668.1:2015 |  | The use of ventilation and airconditioning in Buildings Part 1: Fire and Smoke Control in buildings | [5 empty] | AS1668.1:2015 | The use of ventilation and airconditioning in Buildings Part 1: Fire and Smoke Control in buildings
| AS1668.2:2012 |  | The use of ventilation and air conditioning in buildings Part 2: Mechanical ventilation for acceptable indoor-air quality | [5 empty] | AS1668.2:2012 | The use of ventilation and air conditioning in buildings Part 2: Mechanical ventilation for acceptable indoor-air quality
| AS1668.4:2012 |  | The use of ventilation and air conditioning in buildings Part 4: Natural ventilation of the buildings | [5 empty] | AS1668.4:2012 | The use of ventilation and air conditioning in buildings Part 4: Natural ventilation of the buildings
[9 empty] | AS4674:2004 | Design, construction and fit-out of food premises, Clause 2.5.2
[9 empty] | AS5149.1:2016 | Refrigerating systems and heat pumps - Safety and environmental requirements Part 1: Definitions, classification and selection criteria
[9 empty] | AS5149.2:2016 | Refrigerating systems and heat pumps - Safety and environmental requirements Part 2: Design, construction, testing, marking and documentation
[9 empty] | AS3666.1:2011 | Air-handling and water systems of buildings — Microbial control
• | Fire Engineering Report prepared by BCA Logic (Document No.: 110942-FER-r5)
• | Carppark Ventilation CFD Assessment prepared by i-Fire (Document No.: 20-087XA77)
The following is a schedule of the relevant service design drawings and specifications.
| Drawing Number |  | Drawing Name |  |  |  | Revision
| M-000 |  | COVER SHEET, DRAWINGS LIST, LEGEND AND NOTES |  |  |  | C
| M-001 |  | SPECIFICATION |  |  |  | C
| M-002 |  | EQUIPMENT SCHEDULES |  |  |  | C
| M-003 |  | DETAILS |  |  |  | C
| M-100 |  | BASEMENT 2 LAYOUT |  |  |  | C
| M-101 |  | BASEMENT 1 LAYOUT |  |  |  | C
| M-200 |  | GROUND FLOOR LAYOUT |  |  |  | C
| M-201 |  | LEVEL 1 LAYOUT |  |  |  | C
| M-202 |  | LEVEL 2 LAYOUT |  |  |  | C
| M-203 |  | LEVEL 3 LAYOUT |  |  |  | C
| M-204 |  | LEVEL 4 LAYOUT |  |  |  | C
| M-205 |  | LEVEL 5 LAYOUT |  |  |  | C
| M-206 |  | LEVEL 6 LAYOUT |  |  |  | C
| M-207 |  | LEVEL 7 LAYOUT |  |  |  | C
| M-208 |  | ROOF LAYOUT |  |  |  | C
| M-300 |  | SCHEMATIC |  |  |  | C
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 | [5 empty] | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 |  | 0 |  |  |  | 0
| 0 | [5 empty] | 0
Yours faithfully,
Name: |  | Qing Ye (Felix) |  |  | Date: | 2024-03-12
Note: drawing list auto-copied from '01-Project Info' section.
Please select the clauses from the following list to suit the porject.
Note: manually input project specific building information

## Mech Design Compliance Cert
Mechanical Design Compliance Certificate
Pursuant to the provisions of Clause A5.2 of the Building Code of Australia Amendament 1, Volume 1.
I | Qing Felix Ye |  | of | Premium Consulting Engineers
| (Appropriately qualified person) |  |  | (Firm)
Suite 802, 299 Sussex Street, Sydney NSW 2000
(Address)
Qualifications and experience:
Master of HVAC Engineering, Chartered Professional Engineer (MIEAust No.: 3631369);
NSW Fair Trading C9 Certifier (Reg No.: BDC04672); and
NSW Fair Trading Mechanical Design Practitioner (Reg No.: DEP0000275)
Hereby certify:
The Mechanical system installation on site to date has to the best of our knowledge and belief, confirmed that the works designed and installed have been in accordance with the requirements of the design intent expressed in the design prepared by Premium Consulting Engineers Pty Ltd.
Subject to effective and thorough implementation of advice issued by Premium Consulting Engineers and to the extent that can reasonably be expected based on our inspections of visible work, we confirm our opinion that the works appear to have been undertaken in accordance with the intent of our documentation.
The following is a schedule of the relevant service design drawings and specifications.
| Drawing Number |  | Drawing Name |  |  |  | Revision
| M-000 |  | Cover Sheet |  |  |  | A
| M-001 |  | Tenancy Level Layout |  |  |  | A
| M-002 |  | Roof Layout |  |  |  | A
Yours faithfully,
Name: |  | Qing Ye (Felix) |  |  | Date: | 2024-03-12

## 01-AC Load
Load Calculation | [5 empty] | AC selection |  |  | Grille sizing
Room Name | Unit | Load rate | Cooling Load | Room Total Cooling | Room Total OA | FCU Modle | Cooling | Air Flow | Room Air flow | Grille Qty | Grille flowrate | Grille Size Rounded
|  | W/m2 | kW | kW | l/s |  | kW | l/s | l/s | # | l/s | l/s
TENANCY, AREA 1
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | FDYAN100AV1 | 10 | 800 | 800 | 2 | 400
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
TOTAL | 0 | - |  | 0 | 0 | Total FCU Capacity: | 10 | 800 |  | 7 | 400 | 0
[5 empty] | 0 | VRV CU Selection
[6 empty] | PLEASE SELECT | 0 | -
TENANCY, AREA 2
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 2 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
| 0 | 0 | 0
Equipment |  |  | 0
Water |  |  | 0
Light | 0 | 15 | 0
People | 0 | 120 | 0
O/A=E/A | 0 | 0.0305 | 0
Summary | 0 | - |  | 0 | 0 | PLEASE SELECT | 0 | 0 | 0 | 1 | 0
TOTAL | 0 | - |  | 0 | 0 | Total FCU Capacity: | 0 | 0 |  | 7 | 0 | 0
[5 empty] | 0 | VRV CU Selection
[6 empty] | PLEASE SELECT | 0 | -

## 02-Ventilation Rate
Room Name | Type | Area | Load rate | Air flow
|  | m2 | W/m2 | L/s
50
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Examples
Toilet | Exhaust | 8 | 10 | 80
Gabage room | Exhaust | 10 | 5 | 100
Grease Arrestor | Exhaust | 15 | 5 | 100
Plant room | Exhaust/Supply | 15 | 5 | 100
Main Switch room | Supply | 15 | 5 | 75
Distribuiotn Borad room | Supply | 15 | 5 | 75
Stoage | Supply | 10 | 5 | 50
Lobby/Corridor | Supply | 55 | 1 | 55

## 02a-Nat Vent
Key: | Project Details | Project: |  | Rouse Road
| Input | #: |  | Basement Carpark
| Calculation | Date: |  | 2024-03-12
| Output | Designed By: |  | STC
| Total Number of Spaces | 152
Nat Vent Details
|  | Length | Height (m) | Free Area (m2) | Total Free Area (m2) | Total Allowable Car Parking Spaces |  | Parking goal for Nat Vent
| North Perimeter |  |  | 60% | -10 | -5 | (EXCLUDES MAKE-UP AIR FOR EXHAUST SYSTEM
| South Perimiter |  |  | 60% | 0 | 0 |  | 82
| West Perimiter |  |  | 60% | 18 | 36
31
Exhaust System Details
Remaining Car Parking Spaces Requiring Mech Exhaust
| 70 | Spaces
include clearance details

## 02b-Carpark Vent
Key: | Project Details | Project: |  |  |  | 32631-18-24 RAILWAY ST LIDCOMBE
| Input | #: |  |  |  | B4-GF CARPARK
| Calculation | Date: |  |  |  | 2024-03-12
| Output | Designed By: |  |  |  | SHL
Functional Space | Description | Area (m²) | P1 | P2 | n1 | d1 | n2 | d2 | C1 | C2 | E | F | T1 | T2 | (A) 0.85xC1xExT1 | (B) 0.85xC2xExT2 | (a) 0.85xCxExT (l/s) | (b) 2000xFxT (l/s) | (c) 2.5xA (l/s) | Min Exhaust Air (l/s) | 10% Safety Margin (m3/s) | Supply Air @ 85% of E/A (m3/s) | Note: 10% margin take out
1 | [24 empty] | Exhaust Riser |  |  | Supply Riser
2 | [24 empty] | 2.337 | m2 |  | 1.9865 | m2
3 | B1 | 1288 | 0.3 | 0.3 | 40 | 80 | 92 | 110 | 2160 | 3036 | 1 | 1 | 1 | 1 | 1836 | 2580.6 | 4416.6 | 2000 | 3220 | 4416.6 | 4.5 | 3.825
4 | B2 | 1434 | 0.3 | 0.3 | 45 | 80 | 47 | 110 | 2430 | 1551 | 1 | 1 | 1 | 1 | 2065.5 | 1318.35 | 3383.85 | 2000 | 3585 | 3585 | 3.585 | 3.0473
5 | B3 | 1403 | 0.3 | 0.3 | 47 | 80 | 0 | 0 | 2538 | 0 | 1 | 1 | 1 | 1 | 2157.3 | 0 | 2157.3 | 2000 | 3507.5 | 3507.5 | 3.6 | 3.06
Sub-Total | [20 empty] | 11.685 | 9.9322
Other Vehicle Exhausts
Queing Area | [19 empty] | 0 | 0 | 0
Sub-Total
[23 empty] | 4.0897 | m2 | Exhaust louvre size
Total | [20 empty] | 11.685 | 9.9322 | 6.6215 | m2 | Intake Louvre Size (based on 1.5 m/s)
AS1669.2 (2012) Carpark Ventilation | [19 empty] | Use of car park | Number of vehicles | Parking usage factor (P) |  | E/A Duct Size |  |  |  |  | Second Branch |  |  |  |  | Third Branch
[20 empty] | Residential | 0 | 0.3 |  | FR m3/s | V (m/s) | A (m2) | X (m) | Y (m)
P | Carpark usage factor Table 4.1 (Res - 0.3, Com - 0.5, Retail - 0.7, Ent/Sports - 1.0, Depots 2.4) | [18 empty] | Commercial | 132 | 0.5 |  | #REF! | 8 | #REF! | 0.8 | #REF! | #REF! | 7.5 | #REF! | 0.3 | #REF! | #REF! | 7.5 | #REF! | 0.4 | #REF!
n1 | No. of parking spaces on level (Sum of cars, motorcycles etc.) | [18 empty] | Retail / food and drinks services | 15 | 0.7 |  | 0.011685 | 7.5 | 0.001558 |  | #DIV/0!
d1 | Ave. exit distance for car on level | [18 empty] | Entertainment / Sport centre | 0 | 1
d2 | Ave. exit distance excluding queueing areas for cars on other level going thru this level | [18 empty] | Vehicle depots | 0 | 2.4 |  | 0 | 7.5 | 0 |  | #DIV/0!
n2 | No. of cars passing through level from other parts of the car park (Sum of cars, motorcycles etc.) | [18 empty] | P - Total | 147 | 0.52041 |  | 0 | 7.5 | 0 |  | #DIV/0!
C | Contaminate Rate
C1 | Contaminant generation rate for cars on the level | [18 empty] | Vehicle type factor | Number of vehicles | Vehicle type factor (T) |  | 0.011685 | 7.5 | 0.001558 |  | #DIV/0!
C2 | Contaminant generation rate for cars on other level going thru this level | [18 empty] | No special vehicle population | 190 | 1
E | Staff Exposure Level | [5 empty] | See Table 4.3 | [12 empty] | Diesel vehicle | 0 | 2.4
F | Staff Usage Factor | [5 empty] | See Table 4.3 | [12 empty] | LPG vehicles | 0 | 1
T | Vehicle Type Factor | [5 empty] | See Table 4.2 | [12 empty] | CNG vehicles | 0 | 1
T1 | Vehicle type factor for cars on level | [18 empty] | Electric powered vehicles | 0 | 0.1
T2 | Vehicle type factor for cars on other level going thru this level | [18 empty] | Motorcycles | 0 | 0.25
A | Area (sqm) | [18 empty] | T - Total | 190 | 1
Result 1m (w) x 1m (l) x 2m (h)

## 02c-Fire Pump Vent
Fire Pump Ventilation Calculation
Engine Model
Rating (Gross Power) | 50 | kW
Engine manufacturers published heat rejection value | 20 | kW
Allowable temperature change | 10 | C
Calculation Constant (Advised by pump suppliers) | 3100
Ventilation Flow (m3/hr) = 3100 x heat rejected (kW) / δT
Ventilation Flow = | 6200 | m3/hr
= | 103.3333 | m3/min
= | 1.7222 | m3/sec
= | 1722.2222 | litres/sec

## 03-Air System Sizer
Absolute roughness - k - for some common materials
[17 empty] | Fluid density (kg/m3) |  | 1.204 |  | Galvanised steel |  | 0.15 | mm
[17 empty] | Duct material |  | Galvanised steel |  | Flexible duct |  | 1 | mm
[17 empty] | Abs. roughness (mm) |  | 0.15 |  | Lagged duct |  | 0.375 | mm
System: | XXX
Level | Room/Grille Type 1 |  |  |  | Room/Grille Type 2 |  |  |  | Room/Grille Type 3 |  |  |  | Room/Grille Type 4 |  |  |  | Total Flow | Duct Branch Sizer | [7 empty] | Total Flow | Duct Riser Sizer | [7 empty] | Nos. of Grille | Air Flow | Grille Sizer
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow |  | Width | Height | Face Velocity | ε | Dh | Re | Fd | Fric Loss |  | Width | Height | Face Velocity | ε | Dh | Re | Fd | Fric Loss |  |  | Width | Height | Area Ratio | Face velocity | Act, Velocity
| Room/Grille Type 1 Rate: L/s; Room/Grille Type 1 Flow: L/s; Room/Grille Type 2 Rate: L/s; Room/Grille Type 2 Flow: L/s; Room/Grille Type 3 Rate: L/s; Room/Grille Type 3 Flow: L/s; Room/Grille Type 4 Rate: L/s; Room/Grille Type 4 Flow: L/s | L/s | m | m | m/s | mm | mm |  |  | Pa/m | L/s | m | m | m/s | mm | mm |  |  | Pa/m |  | L/s | m | m | % | m/s | m/s
XXX | Room/Grille Type 1 NO.: 1; Room/Grille Type 1 Rate: 2300; Room/Grille Type 2 NO.: 0; Room/Grille Type 2 Rate: 0; Room/Grille Type 3 NO.: 0; Room/Grille Type 3 Rate: 0; Room/Grille Type 4 NO.: 0; Room/Grille Type 4 Rate: 0
| Room/Grille Type 1 Flow: 2300; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 2300 | 0.95 | 0.35 | 6.9173 | 0.15 | 511.5385 | 234953.8462 | 0.017434 | 0.98174 |  |  |  | - | [5 empty] | 1 | 2300 | 2.5 | 0.5 | 60% | 1.84 | 3.0667
| 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 2 | 0 | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 |  |  | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
| 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Room/Grille Type 1 Flow: 0; Room/Grille Type 2 Flow: 0; Room/Grille Type 3 Flow: 0; Room/Grille Type 4 Flow: 0 | 0 | 0 | 0 | - | 0.15 | - | - | - | - | 2300 | 0 | 0 | - | 0.15 | - | - | - | - | 0 | - | 0 | 0 | 50% | - | -
Note on W7: Freeman J: Material absolute roughness factor (mm) - ε
Note on X7: Freeman J: Hydraulic diameter (mm) - Dh
Note on Y7: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on Z7: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AA7: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AG7: Freeman J: Material absolute roughness factor (mm) - ε
Note on AH7: Freeman J: Hydraulic diameter (mm) - Dh
Note on AI7: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AJ7: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AK7: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation

## 04a-Basement Stair Press
Stair pressurisation Calculation
Project: | 58-68 Regent St. Kogarah
Project Number: | 912167
System Ref. | FPSF-R-1,2
Stair Ref | FS 3 and 4
Open Door Number | 2
Main Discharge Door Number | 1
Number of closed doors | 8 |  | Note: FS 1 from G to L10, Total 11 of floors. Eliminating the 3 open doors (fire affect level, above level and level 1 exit), the number of closed doors equates to 8.
Closed Door Leakage Factor | 0.0416 | m3/sec
Stair Perimeter | 12 | m
Stair Height | 13.2 | m
Wall Area | 158.4 | m2
Wall Leakage Factor | 0.00035 | m/m2
Open Exit Door Flow | 4.1216 | m3/sec
Main Discharge Door Flow | 2.0608 | m3/sec
Shaft Wall Leakage | 0.05544 | m3/sec
Closed Door Leakage | 0.3328 | m3/sec
Sub Total | 6.5706 | m3/sec
Safety Factor (10%) | 0.65706 | m3/sec
Total | 7.2277 | m3/sec | 7227.704 | l/s
Shaft area Require (@ 6 m/s) | 1.2046 | m2
Grille No. | 5 |  | Note: grilles to be on B3 and B2
Grille air flow | 1.4455 | m3/sec
Grille Width | 1.2 | m
Grille Height | 0.9 | m
Face Velocity | 1.3385 | m/sec

## 04b-Tower Stair Press
Stair pressurisation Calculation
Project: | 58-68 Regent St. Kogarah
Project Number: | 912167
System Ref. | FPSF-B1-1
Stair Ref | FS 1
Open Door Number | 2
Main Discharge Door Number | 1
Number of closed doors | 2 |  | Note: FS 1 from B3 to LG, Total 5 of floors. Eliminating the 3 open doors (fire affect level, above level and level 1 exit), the number of closed doors equates to 2.
Closed Door Leakage Factor | 0.0416 | m3/sec
Stair Perimeter | 10 | m
Stair Height | 13.2 | m
Wall Area | 132 | m2
Wall Leakage Factor | 0.00035 | m/m2
Open Exit Door Flow | 4.1216 | m3/sec
Main Discharge Door Flow | 2.0608 | m3/sec
Shaft Wall Leakage | 0.0462 | m3/sec
Closed Door Leakage | 0.0832 | m3/sec
Sub Total | 6.3118 | m3/sec
Safety Factor (10%) | 0.63118 | m3/sec
Total | 6.943 | m3/sec | 6942.98 | l/s
Shaft area Require (@ 6 m/s) | 1.1572 | m2
Grille No. | 2 |  | Note: grilles to be on B3 and B2
Grille air flow | 3.4715 | m3/sec
Grille Width | 2 | m
Grille Height | 0.9 | m
Face Velocity | 1.9286 | m/sec

## 05-Tower Stair Relief
Stair pressurisation Relief Calculation
Project: | 58-68 Regent St. Kogarah
Project Number: | 912167
System Ref. | FPSF-R-1,2
Stair Ref | FS 3 and 4
Number of doors to relieve | 2
Relief Airflow from door | 4.136 | m3/sec
Assumed leakage closed damper | 0.05 | m3/sec
MASONRY Duct Sizer
Number of closed damper | 20 |  |  | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss
|  |  |  | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m
Leakage through closed dampers | 1 | m3/sec | 1 | 5000 | 0.8 | 0.8 | 7.8125 | 1 | 800 | 415000 | 0.021489 | 0.98695
|  |  | 2 |  |  |  | - | 1 | - | - | - | -
Subtotal for shaft | 5.136 | m3/sec | 3 |  |  |  | - | 1 | - | - | - | -
|  |  | 4 |  |  |  | - | 1 | - | - | - | -
Saftey Factor (25%) | 1.284 | m3/sec | 5 |  |  |  | - | 1 | - | - | - | -
|  |  | 6 |  |  |  | - | 1 | - | - | - | -
Total Through Shaft | 6.42 | m3/sec | 7 |  |  |  | - | 1 | - | - | - | -
|  |  | 8 |  |  |  | - | 1 | - | - | - | -
Shaft Size requirements (@7 m/s) | 0.91714 | m2
Sub Duct | 4.136 | m3/sec
Shaft Size requirements (@7 m/s) | 0.8272 | m2
shaft Size | 1.7443 | m2
Note on M15: Freeman J: Material absolute roughness factor (mm) - ε
Note on N15: Freeman J: Hydraulic diameter (mm) - Dh
Note on O15: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on P15: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on Q15: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation

## 06-Casual Duct Sizer
Absolute roughness - k - for some common materials
[12 empty] | Fluid density (kg/m3) |  | 1.204 |  | Galvanised steel | 0.15 | mm
[12 empty] | Duct material |  | Flexible duct |  | Flexible duct | 0.3 | mm
[12 empty] | Abs. roughness (mm) |  | 0.3 |  | Lagged duct | 0.375 | mm
[16 empty] | Ordinary concrete | 1 | mm
[16 empty] | Coarse concrete | 5 | mm
[16 empty] | Stainless steel | 0.006 | mm
METAL Duct Sizer | [9 empty] | MASONRY Duct Sizer | [9 empty] | FLEX Duct Sizer | [8 empty] | GRILLE Sizer
| Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Flex size | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Grille size |  | % | Face velocity | Act, Velocity
| L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | Dia/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m |  | m/s | m/s
1 | 50 | 0.2 | 0.15 | 1.6667 | 0.15 | 171.4286 | 18971.4286 | 0.028149 | 0.27458 | 1 | 8400 | 0.7 | 1.6 | 7.5 | 1 | 973.913 | 485008.6957 | 0.02049 | 0.71241 | 1 | 300 | 0.3 | 4.2382 | 1 | 300 | 84424.6662 | 0.028654 | 1.0328 | 1 | 130 | 0.41 | 0.17 | 50% | 1.8651 | 3.7303
2 |  |  |  | - | 0.15 | - | - | - | - | 2 | 4200 | 0.7 | 0.98 | 6.1224 | 1 | 816.6667 | 332000 | 0.021549 | 0.59544 | 2 |  |  | - | 1 | 0 | - | - | - | 2 |  |  |  | 50% | - | -
3 |  |  |  | - | 0.15 | - | - | - | - | 3 |  |  |  | - | 1 | - | - | - | - | 3 |  |  | - | 1 | 0 | - | - | - | 3 |  |  |  | 50% | - | -
4 |  |  |  | - | 0.15 | - | - | - | - | 4 |  |  |  | - | 1 | - | - | - | - | 4 |  |  | - | 1 | 0 | - | - | - | 4 |  |  |  | 50% | - | -
5 |  |  |  | - | 0.15 | - | - | - | - | 5 |  |  |  | - | 1 | - | - | - | - | 5 |  |  | - | 1 | 0 | - | - | - | 5 |  |  |  | 50% | - | -
6 |  |  |  | - | 0.15 | - | - | - | - | 6 |  |  |  | - | 1 | - | - | - | - | 6 |  |  | - | 1 | 0 | - | - | - | 6 |  |  |  | 50% | - | -
7 |  |  |  | - | 0.15 | - | - | - | - | 7 |  |  |  | - | 1 | - | - | - | - | 7 |  |  | - | 1 | 0 | - | - | - | 7 |  |  |  | 50% | - | -
8 |  |  |  | - | 0.15 | - | - | - | - | 8 |  |  |  | - | 1 | - | - | - | - | 8 |  |  | - | 1 | 0 | - | - | - | 8 |  |  |  | 50% | - | -
METAL Duct Size Table | [9 empty] | MASONRY Duct Size Table | [9 empty] | FLEX Duct Size Table | [8 empty] | GRILLE Size
| Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Duct size |  | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Flex size | Velocity | ε | Dh | Re | Fd | Fric Loss |  | Flow rate | Grille size |  | % | Face velocity | Act, Velocity
| L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m | m/s | mm | mm |  |  | Pa/m |  | L/s | Dia/m | m/s | mm | mm |  |  | Pa/m |  | L/s | W/m | H/m |  | m/s | m/s
1 | 100 | 0.25 | 0.15 | 2.6667 | 0.15 | 187.5 | 33200 | 0.025175 | 0.57478 | 1 | 200 | 0.25 | 0.25 | 3.2 | 1 | 250 | 53120 | 0.030708 | 0.75718 | 1 | 55 | 0.15 | 3.108 | 1 | 150 | 30955.711 | 0.036037 | 1.397 | 1 | 20 | 0.15 | 0.15 | 50% | 0.88889 | 1.7778
2 | 200 | 0.4 | 0.15 | 3.3333 | 0.15 | 218.1818 | 48290.9091 | 0.02336 | 0.71616 | 2 | 500 | 0.35 | 0.35 | 4.0816 | 1 | 350 | 94857.1429 | 0.027473 | 0.78724 | 2 | 120 | 0.2 | 3.8144 | 1 | 200 | 50654.7997 | 0.032509 | 1.4237 | 2 | 40 | 0.2 | 0.2 | 50% | 1 | 2
3 | 400 | 0.5 | 0.2 | 4 | 0.15 | 285.7143 | 75885.7143 | 0.021294 | 0.71785 | 3 | 1000 | 0.45 | 0.45 | 4.9383 | 1 | 450 | 147555.5556 | 0.025395 | 0.82849 | 3 | 195 | 0.25 | 3.9669 | 1 | 250 | 65851.2397 | 0.030327 | 1.1492 | 3 | 60 | 0.25 | 0.25 | 50% | 0.96 | 1.92
4 | 600 | 0.5 | 0.25 | 4.8 | 0.15 | 333.3333 | 106240 | 0.020036 | 0.83369 | 4 | 2000 | 0.6 | 0.6 | 5.5556 | 1 | 600 | 221333.3333 | 0.023406 | 0.7248 | 4 | 250 | 0.3 | 3.5318 | 1 | 300 | 70353.8885 | 0.028937 | 0.72431 | 4 | 70 | 0.3 | 0.3 | 50% | 0.77778 | 1.5556
5 | 800 | 0.6 | 0.25 | 5.3333 | 0.15 | 352.9412 | 124988.2353 | 0.019512 | 0.94668 | 5 | 5000 | 0.85 | 0.85 | 6.9204 | 1 | 850 | 390588.2353 | 0.021245 | 0.72061 | 5 | 355 | 0.35 | 3.6846 | 1 | 350 | 85630.7329 | 0.027623 | 0.64505 | 5 | 80 | 0.3 | 0.3 | 50% | 0.88889 | 1.7778
6 | 1000 | 0.8 | 0.25 | 5 | 0.15 | 380.9524 | 126476.1905 | 0.01933 | 0.76366 | 6 | 10000 | 1.1 | 1.1 | 8.2645 | 1 | 1100 | 603636.3636 | 0.019835 | 0.74142 | 6 | 500 | 0.4 | 3.9733 | 1 | 400 | 105530.8328 | 0.026503 | 0.6297 | 6 | 90 | 0.35 | 0.35 | 50% | 0.73469 | 1.4694
7 | 1500 | 1 | 0.3 | 5 | 0.15 | 461.5385 | 153230.7692 | 0.018513 | 0.60368 | 7 | 15000 | 1.25 | 1.25 | 9.6 | 1 | 1250 | 796800 | 0.01916 | 0.85042 | 7 | 600 | 0.45 | 3.7673 | 1 | 450 | 112566.2217 | 0.025731 | 0.48853 | 7 | 100 | 0.4 | 0.4 | 50% | 0.625 | 1.25
8 | 2000 | 1.2 | 0.3 | 5.5556 | 0.15 | 480 | 177066.6667 | 0.01812 | 0.70139 | 8 | 20000 | 1.4 | 1.4 | 10.2041 | 1 | 1400 | 948571.4286 | 0.018627 | 0.83399 | 8 | [8 empty] | 8 | 120 | 0.4 | 0.4 | 50% | 0.75 | 1.5
Note on F14: Freeman J: Material absolute roughness factor (mm) - ε
Note on G14: Freeman J: Hydraulic diameter (mm) - Dh
Note on H14: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on I14: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on J14: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Q14: Freeman J: Material absolute roughness factor (mm) - ε
Note on R14: Freeman J: Hydraulic diameter (mm) - Dh
Note on S14: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on T14: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on U14: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AA14: Freeman J: Material absolute roughness factor (mm) - ε
Note on AB14: Freeman J: Hydraulic diameter (mm) - Dh
Note on AC14: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AD14: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AE14: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on F34: Freeman J: Material absolute roughness factor (mm) - ε
Note on G34: Freeman J: Hydraulic diameter (mm) - Dh
Note on H34: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on I34: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on J34: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on Q34: Freeman J: Material absolute roughness factor (mm) - ε
Note on R34: Freeman J: Hydraulic diameter (mm) - Dh
Note on S34: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on T34: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on U34: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation
Note on AA34: Freeman J: Material absolute roughness factor (mm) - ε
Note on AB34: Freeman J: Hydraulic diameter (mm) - Dh
Note on AC34: Freeman J: ASHRAE Fundamental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Note on AD34: Freeman J: Friction Loss calculation: Colebrook Equation Approximations Swamee and Jain Equation (1976)
Note on AE34: Freeman J: ASHRAE Fundamental 2017: Darcy–Weisbach equation

## 07-Casual Pipe Sizer
Chilled Water Pipe Sizer |  | Cooling/Condensate Water Pipe Sizer |  | Heating Hot Water Pipe Sizer |  | AC Condensate Water Pipe Sizer
Flow Rate | Diameter | Flow Rate | Diameter | Flow Rate | Diameter | Cooling Load | Diameter
2.25 | 65 | 14 | 100 | 0.01 | 15 | 44.5 | 32
3.51 | 80 | 14.01 | 125 | 0.04 | 20 | 100 | 40
5.8 | 80 | 14.1 | 125 | - | - | 101 | 40
- | - | 25 | 125 | - | - | - | -
- | - | - | - | - | - | - | - |  |  | Type | ID | Parameter | Lowest In Range | Highest In Range | Diameter
- | - | - | - | - | - | - | - |  |  |  |  | < L/s | L/s | L/s | mm
- | - | - | - | - | - | - | -
- | - | - | - | - | - | - | -
[10 empty] | Chilled water pipe size | chilled_water_pipe | 12.51 | 5.81 | 12.51 | 100
Chilled Water Pipe Size Lookup Table |  | Cooling/Condensate Water Pipe Lookup Table |  | Heating Hot Water Pipe Lookup Table |  | AC Condensate Water Pipe Lookup Table |  | Pipe Size Guide | Type ID | Chilled water pipe size | chilled_water_pipe | 23.01 | 12.51 | 23.01 | 125
Flowrate (l/s) | DN(mm) | Flowrate (l/s) | DN(mm) | Flowrate (l/s) | DN(mm) | Cooling Load (kW) | DN(mm) | Chilled | chilled_water_pipe | Chilled water pipe size | chilled_water_pipe | 38.01 | 23.01 | 38.01 | 150
0.04 | 15 | 0.04 | 15 | 0.04 | 15 | 7 | 20 | Hot Water | hot_water_pipe | Chilled water pipe size | chilled_water_pipe | 78.01 | 38.01 | 78.01 | 200
0.12 | 20 | 0.12 | 20 | 0.12 | 20 | 17.6 | 25 | Condenser Water | condenser_water_pipe | Chilled water pipe size | chilled_water_pipe | 121.1 | 78.01 | 121.1 | 250
0.26 | 25 | 0.28 | 25 | 0.31 | 25 | 100 | 32 |  |  | Chilled water pipe size | chilled_water_pipe | 173.1 | 121.1 | 173.1 | 300
0.51 | 32 | 0.56 | 32 | 0.61 | 32 | 176 | 40 |  |  | Chilled water pipe size | chilled_water_pipe | 209.1 | 173.1 | 209.1 | 350
0.81 | 40 | 0.91 | 40 | 1.01 | 40 | 598 | 50 |  |  | Chilled water pipe size | chilled_water_pipe | 273.1 | 209.1 | 273.1 | 400
2.01 | 50 | 2.11 | 50 | 2.26 | 50 | 1055 | 80 |  |  | Chilled water pipe size | chilled_water_pipe | 345.1 | 273.1 | 345.1 | 450
3.51 | 65 | 3.81 | 65 | 4.41 | 65 | 1512 | 100 |  |  | Chilled water pipe size | chilled_water_pipe | 430.1 | 345.1 | 430.1 | 500
5.81 | 80 | 6.26 | 80 | 7.01 | 80 | 12462 | 125 |  |  | Chilled water pipe size | chilled_water_pipe | 523.1 | 430.1 | 523.1 | 550
12.51 | 100 | 14.01 | 100 | 15.01 | 100 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0 | 0 | 0 | 0
23.01 | 125 | 25.01 | 125 | 27.01 | 125 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.04 | 1e-12 | 0.4 | 15
38.01 | 150 | 40.01 | 150 | 43.01 | 150 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.12 | 0.4 | 0.12 | 20
78.01 | 200 | 80.01 | 200 | 80.01 | 200 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.31 | 0.12 | 0.26 | 25
121.1 | 250 | 125.1 | 250 | 125.1 | 250 |  |  |  |  | Hot water pipe size | hot_water_pipe | 0.61 | 0.26 | 0.51 | 32
173.1 | 300 | 173.1 | 300 | 173.1 | 300 |  |  |  |  | Hot water pipe size | hot_water_pipe | 1.01 | 0.51 | 0.81 | 40
209.1 | 350 | 209.1 | 350 | 209.1 | 350 |  |  |  |  | Hot water pipe size | hot_water_pipe | 2.26 | 0.81 | 2.01 | 50
273.1 | 400 | 273.1 | 400 | 273.1 | 400 |  |  |  |  | Hot water pipe size | hot_water_pipe | 4.41 | 2.01 | 3.51 | 65
345.1 | 450 | 345.1 | 450 | 345.1 | 450 |  |  |  |  | Hot water pipe size | hot_water_pipe | 7.01 | 3.51 | 5.81 | 80
430.1 | 500 | 430.1 | 500 | 430.1 | 500 |  |  |  |  | Hot water pipe size | hot_water_pipe | 15.01 | 5.81 | 12.51 | 100
523.1 | 550 | 523.1 | 550 | 523.1 | 550 |  |  |  |  | Hot water pipe size | hot_water_pipe | 27.01 | 12.51 | 23.01 | 125
623 | 600 | 623 | 600 | 623 | 600 |  |  |  |  | Hot water pipe size | hot_water_pipe | 43.01 | 23.01 | 38.01 | 150
[10 empty] | Hot water pipe size | hot_water_pipe | 80.01 | 38.01 | 78.01 | 200
[10 empty] | Hot water pipe size | hot_water_pipe | 125.1 | 78.01 | 121.1 | 250
[10 empty] | Hot water pipe size | hot_water_pipe | 173.1 | 121.1 | 173.1 | 300
[10 empty] | Hot water pipe size | hot_water_pipe | 209.1 | 173.1 | 209.1 | 350
[10 empty] | Hot water pipe size | hot_water_pipe | 523.1 | 430.1 | 523.1 | 550
[10 empty] | Condenser water pipe size | condenser_water_pipe | 523.1 | 430.1 | 523.1 | 550
[10 empty] | Condenser water pipe size | condenser_water_pipe | 623 | 523.1 | 623 | 600

## REF (hidden)
Duct Length (m) - L | 6 | m
Duct Width (mm) - a | 500 | mm
Duct Height (mm) - b | 300 | mm
Hydraulic diameter (mm) - Dh | 375 | mm
Equivalent Diameter (mm) - De | 419.9793 | mm
Airflow (l/s) - Q | 735 | l/s
Airflow (m3/s) - Q | 0.735 | m3/s
Velocity (m/s) - v | 4.9 | m/s
Air density (kg/m3) - ρ | 1.204 | kg/m3
Material absolute roughness factor (mm) - ε | 0.15 | mm | Galvanized steel 0.15mm; Ordinary concrete 0.3-1mm
Reynolds Number | 122010 |  | ASHRAE Fundemental 2017: for standard air and temperature between 4 and 38°C, Re can be calculated by Re=66.4 DhV
Darcy–Weisbach friction factor - f (Swamee and Jain) | 0.019449 |  | Colebrook Equation Approximations
Darcy–Weisbach friction factor - f (Haaland) | 0.019126 |  |  | Swamee and Jain Equation (1976) | Haaland (1983) | Tsai（1989）
Darcy–Weisbach friction factor - f (Tsai) | 0.019349
Imperical friction loss (Pa/m) | 0.79254 | Pa/m
Calcualtion Method | Tsai |  | Imperical
Friction Loss (Pa/m) | 0.74579 | Pa/m | Swamee Jain
Friction Loss Section (Pa) -ΔP | 4.4747 | Pa | Haaland |  |  | Imperical
Tsai

## REF-AC Data
System | Type | CU/FCU | Model Number | Nominal Cooling Capacity(kW) | Nominal Heating Capacity(kW) | Nominal Air Flow (l/s) | Highest Air Flow (l/s)
SPC | Split Ducted Standard | FCU | FDYAN50AV1 | 5 | 6 | 370 | 370
SPC | Split Ducted Standard | FCU | FDYAN60AV1 | 6 | 7 | 400 | 400
SPC | Split Ducted Standard | FCU | FDYAN71AV1 | 7.1 | 7.5 | 566 | 566
SPC | Split Ducted Standard | FCU | FDYAN85AV1 | 8.5 | 10 | 600 | 600
SPC | Split Ducted Standard | FCU | FDYAN100AV1 | 10 | 12.5 | 800 | 800
SPC | Split Ducted Standard | FCU | FDYAN125AV1 | 12.5 | 15 | 840 | 840
SPC | Split Ducted Standard | FCU | FDYAN140AV1 | 14 | 16.5 | 1000 | 1000
SPC | Split Ducted Standard | FCU | FDYAN160AV1 | 15.5 | 18 | 1120 | 1120
SPC | Split Ducted Standard | FCU | FDYQN180LCV1 | 18 | 20 | 1200 | 1200
SPC | Split Ducted Standard | FCU | FDYQN200LCV1 | 19.5 | 22.4 | 1600 | 1600
SPC | Split Ducted Standard | FCU | FDYQN250LBV1 | 23.5 | 26.8 | 1600 | 1600
SPC | Split Ducted Low Profile | FCU | FBA50BAVMA | 5 | 6 | 300 | 300
SPC | Split Ducted Low Profile | FCU | FBA60BAVMA | 6 | 7.1 | 300 | 300
SPC | Split Ducted Low Profile | FCU | FBA71BVMA | 7.1 | 8 | 383 | 383
SPC | Split Ducted Low Profile | FCU | FBA85BVMA | 8.5 | 10 | 533 | 533
SPC | Split Ducted Low Profile | FCU | FBA100BVMA | 10 | 11.2 | 533 | 533
SPC | Split Ducted Low Profile | FCU | FBA125BVMA | 12.5 | 14 | 600 | 600
SPC | Split Ducted Low Profile | FCU | FBA140BVMA | 14 | 16 | 600 | 600
VRV | STANDARD DUCTED TYPE | FCU | FXMQ20PAVE | 2.2 | 2.5 | 150 | 150
VRV | STANDARD DUCTED TYPE | FCU | FXMQ25PAVE | 2.8 | 3.2 | 150 | 150
VRV | STANDARD DUCTED TYPE | FCU | FXMQ32PAVE | 3.6 | 4 | 158 | 158
VRV | STANDARD DUCTED TYPE | FCU | FXMQ40PAVE | 4.5 | 5 | 267 | 267
VRV | STANDARD DUCTED TYPE | FCU | FXMQ50PAVE | 5.6 | 6.3 | 300 | 300
VRV | STANDARD DUCTED TYPE | FCU | FXMQ63PAVE | 7.1 | 8 | 325 | 325
VRV | STANDARD DUCTED TYPE | FCU | FXMQ80PAVE | 9 | 10 | 417 | 417
VRV | STANDARD DUCTED TYPE | FCU | FXMQ100PAVE | 11.2 | 12.5 | 533 | 533
VRV | STANDARD DUCTED TYPE | FCU | FXMQ125PAVE | 14 | 16 | 650 | 650
VRV | STANDARD DUCTED TYPE | FCU | FXMQ140PAVE | 16 | 18 | 767 | 767
VRV | STANDARD DUCTED TYPE | FCU | FXMQ160PV1A | 18 | 20 | 1120 | 1120
VRV | STANDARD DUCTED TYPE | FCU | FXMQ180PV1A | 20 | 22.4 | 1160 | 1160
VRV | STANDARD DUCTED TYPE | FCU | FXMQ200PV1A | 22.4 | 25 | 1200 | 1200
VRV | STANDARD DUCTED TYPE | FCU | FXMQ250PV1A | 28 | 31.5 | 1400 | 1400
VRV | WARDROBE TYPE | FCU | FXDQ20TV1B | 2.2 | 2.5 | 135 | 135
VRV | WARDROBE TYPE | FCU | FXDQ25TV1B | 2.8 | 3.2 | 150 | 150
VRV | WARDROBE TYPE | FCU | FXDQ32TV1B | 3.6 | 4 | 150 | 150
VRV | WARDROBE TYPE | FCU | FXDQ40TV1B | 4.5 | 5 | 210 | 210
VRV | WARDROBE TYPE | FCU | FXDQ50TV1B | 5.6 | 6.3 | 250 | 250
VRV | WARDROBE TYPE | FCU | FXDQ63TV1B | 7.1 | 8 | 333 | 333
PLEASE SELECT
VRV | VRV IV S | CU | RXYMQ3AV4A | 9 | 10
VRV | VRV IV S | CU | RXYMQ4AV4A | 11.2 | 12.5
VRV | VRV IV S | CU | RXYMQ5AV4A | 14 | 14
VRV | VRV IV S | CU | RXYMQ6AV4A | 16 | 16
VRV | VRV IV S | CU | RXYMQ8AV4A | 22.4 | 22.4
VRV | VRV IV S | CU | RXYMQ9AV4A | 24 | 24
PLEASE SELECT

## Ver.
Revision | Date | Created by | Reviewed by | Description
0.0 | prior to Oct'22 | Felix |  | 1st draft from previous adhoc calc
0.1 | 2022-11-08 | Freeman |  | Consolidated version referencing 'Preliminary Calculation'
0.2 | 2023-02-13 | Freeman |  | 05-Tower Stair Relief' added MASONRY Duct Sizer
0.3 | 2023-05-04 | Daniel |  | 07-Design Checklist, pending 0.4rev update correct description
0.3 | 2024-02-26 | Felix Ye |  | Delete design checklist, Adding design cert and design compliance cert
Table of Content
01 | AC Load Estimation
02 | Ventilation Rate
02a | Natural Ventilation
02b | Carpark Ventilation
02c | Fire Pump Ventilation
03 | Air Duct System Sizer
04a | Basement Stair Pressurisation
04b | Tower Stair Pressurisation
05 | Tower Stair Relief
Duct Size Chart
Pipe Size Chart
REF-AC Data

## Sheet2 (hidden)
Level | Room Type 1 |  |  |  | Room Type 2 |  |  |  | Room Type 3 |  |  |  | Room Type4 |  |  |  | Room Type 5 |  |  |  | Room Type 6 |  |  |  | Room Type 7 |  |  |  | Room Type 8
| NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow | NO. | Room | Rate | Flow
| Room Type 1 Rate: L/s; Room Type 1 Flow: L/s; Room Type 2 Rate: L/s; Room Type 2 Flow: L/s; Room Type 3 Rate: L/s; Room Type 3 Flow: L/s; Room Type4 Rate: L/s; Room Type4 Flow: L/s; Room Type 5 Rate: L/s; Room Type 5 Flow: L/s; Room Type 6 Rate: L/s; Room Type 6 Flow: L/s; Room Type 7 Rate: L/s; Room Type 7 Flow: L/s; Room Type 8 Rate: L/s; Room Type 8 Flow: L/s | Rate | Flow
B1 | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 50; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 | L/s | L/s
|  |  |  | 50 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
G | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 30; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 |  | #REF!
|  |  |  | 30 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
L1 | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 30; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 |  | #REF!
|  |  |  | 30 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
L2 | Room Type 1 NO.: 1; Room Type 1 Room: Cleaning; Room Type 1 Rate: 30; Room Type 2 NO.: 1; Room Type 2 Room: staff WC; Room Type 2 Rate: 40 |  | #REF!
|  |  |  | 30 |  |  |  | 40 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| Room Type 2 Room: #REF!; Room Type 3 Room: #REF!; Room Type4 Room: #REF!; Room Type 5 Room: #REF!; Room Type 6 Room: #REF!; Room Type 7 Room: #REF!; Room Type 8 Room: #REF! |  | #REF!